{"text_format":"2","workbook":"xls","n_sheets":33,"sheets":["Use of Calculated Pulling Tensi","Inst  for Cable Pull","Product Sheets","Illustration","Form for a cable pull calc","Calc for 600V","VoP","600V Cable Pull Comparison","Terms and Conditions","Calc for Power Cable","Power Cable Pull Comparison","NEC GW 250.66"," Sketch for 600V wire","Sketch for Power Cable","Dropdown","Supplied to BEM","Maxis Grips","Tension Calc","Power Cable Tension Calc ","Conduit","Voltage Drop NEC Table 9","Jackets","Conductor","Conductor Aux","Conductor PC Comp","Power Cable Comp Calc","Reels","BEM Reels","Products","Reverse","Matrix","Comp Calc","PC REEL Size Data"],"not_rendered":{"charts":0,"images":11,"macros":1,"external_links":1,"defined_names":125,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Use of Calculated Pulling Tensi","index":0,"n_rows":17,"n_cols":1,"rows_kept":17,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
["Use of Calculated Pulling Tensions"]
[]
[]
["Calculations should be made to indicate whether the pull looks “easy” or “impossible,”"]
["making the decision to pull an obvious choice. When a “marginal” situation is"]
["encountered, the entire pull should be reviewed. This review may include more rigorous"]
["calculations or trial pulls. A final decision should be made based on installation factors"]
["known to the end user and installer."]
[]
["The sizes of the conduit are determined based on the calculations of the clearances,"]
["jamming, and fill. Pulling tensions may then be evaluated by determining the maximum"]
["tension based on the pulling device used and the maximum tension that can be applied"]
["to the conductors. The lesser of these two values is the maximum allowable tension (Tm)."]
["The pulling tension (T) required to pull the cable through the conduit is then calculated"]
["and compared to the maximum allowable tension. If the pulling tension exceeds the"]
["allowable tension or sidewall pressure, then conditions should be changed to ensure a successful pull."]

{"sheet":"Inst  for Cable Pull","index":1,"n_rows":52,"n_cols":16,"rows_kept":52,"cut":false,"hidden":true,"merged":[[4,0,7,29],[1,0,1,29]],"flags":["formulas_cached_only"]}
[]
["How to enter a cable pull into the calculator."]
[]
["First, enter the wires going in the conduit.  Next, enter the conduit type and size."]
["Example: 3/C SIMpull CU THHN Size 350, with a 4/0 SIMpull THHN ground wire: in GRC (Galv Rigid Conduit) size 3''.  It is assumed that it takes approx. 25 lbs of force to pull the wire off the reel.  Thus, incoming tension is set at 25 lb and can be changed if needed."]
[]
[]
[]
[]
["A cable pull is divided into segments."]
["A segment is the length of straight section of the pipe and the details of the bend or elbow."]
[]
[null,"IE.  Segment 1   …beginning of conduit to the end of the first bend."]
[null,"      Segment 2   …start of second straight section to the end of the second bend.  "]
[null,"      Last segment will always be the straight section info and no bend section info."]
[]
["A segment has two parts that needs to be captured.  The straight section and the bend section."]
[]
["The straight section consists of three elements: "]
["1.  The Angle (Slope) in degrees.  Zero degrees (left blank)is horizontal."]
[" 90 degrees could be straight up or straight down, ."]
["2.  Wire is being pulled; Up, Down or HZTL (horizontal)."]
["3.  The segment length; is from the beginning of straight section to the end of bend."]
[]
[null,"Example of the straight section:  90 degrees up for 14'.  "]
[null,"      Enter as; Angle (Slope) = 90;  Wire is being pulled = UP: Length ft. = 14."]
[]
["    Note … A horizontally straight section for 30' would be …."]
["          Entered as; Angle (Slope) = (blank); Wire is being pulled = HZTL; Length ft. = 30."]
[]
["The bend section consists of four elements:"]
["1.  The bend type; the direction of the bend / elbow is turning?  "]
[null,"VCDN = Vertical concave turning down"]
[null,"VCUP = Vertical concave turning up"]
[null,"HZTL = Horizontal"]
[]
["2.  Up, Down or N/A : how the wire enters the vertical part of the bend?"]
["Wire is going UP through the bend, Down through the bend, or N/A (horizontally). "]
["  ",{"$nulls":14},"  "]
["3.  The degree of the elbow or bend."]
[null,"90 = 90 degree elbow"]
[]
["4.  The radius of the elbow."]
[null,"STD = standard radius"]
[null,"18 = 18'' sweep radius,"]
[]
["Bend is going down, the wire is going up to the bend, in a 90 degree elbow, with a standard radius."]
[]
["     Enter as: bend type = VCDN; Up, Down, N/A = UP; Angle = 90, Radius = std.    "]
[]
["This first segment will show Tension of 115 lb. and Sidewall Pressure of 74 lb."]
["  ",{"$nulls":14},"  "]

{"sheet":"Product Sheets","index":2,"n_rows":13,"n_cols":2,"rows_kept":13,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["Product sheets for:","Copy and paste the URL address below to your internet browser"]
[]
["SIMpull CU THHN THWN-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet276"]
["SIMpull CU XHHW-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet5"]
["CU USE RHH RHW-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet7"]
[]
["SIMpull Aluminun THHN THWN-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet327"]
["AL XHHW-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet3"]
["AL USE RHH RHW-2","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet12"]
[]
["Southwire's complete Catalog","http://www.southwire.com/processChannel.do?channelId=2dd91dc51235df00VgnVCM1000004c026564RCRD"]
[]
["Maxis Tools Catalog","http://www.maxis-tools.com"]

{"sheet":"Illustration","index":3,"n_rows":51,"n_cols":14,"rows_kept":51,"cut":false,"hidden":true,"merged":[[33,8,33,9],[33,10,33,11],[4,0,5,13],[9,12,11,12],[9,13,11,13],[31,10,31,11],[32,8,32,9],[32,10,32,11],[34,8,34,9],[34,10,34,11],[40,3,43,11],[36,8,36,9],[36,10,36,11],[37,8,37,9],[37,10,37,11],[35,8,35,9],[35,10,35,11]],"flags":["formulas_cached_only"]}
[{"$nulls":4},"                               Wire pull with 6 90's,  2 60's and elevation changes "]
[{"$nulls":4},"                   533' of  3/C 350 and 1/C 4/0 SIMpull CU THHN"]
[{"$nulls":6},"        In 3\" Galvanized Rigid Conduit"]
[]
["Cable Pull Comparison using different Conductors"]
[]
["Total wt./ ft",4.233]
["Configuration","Complex",{"$nulls":6},"COF 0.14",null,"COF 0.35",null,"COF 0.14 ","COF 0.35 "]
["Wt.correction factor",1.4,{"$nulls":6},"Recommended",null,"Not Recommended",null,"Recommended","Not Recommended"]
["COF",0.14,{"$nulls":6},"SIMpull CU THHN",null,"Regular CU THHN",null,"SIMpull AL THHN No Lube Required Colored wires","AL XHHW             Lube Required Black with phase tape"]
["Incoming tension","25",{"$nulls":6},"No Lube Required",null,"Lube Required"]
[{"$nulls":8},"Colored wires",null,"Black with phase tape"]
["Wire pull / Segment","Straight Section Angle (slope / degrees)","Wire is being pulled ..","Segment Length Ft.","Bend Section Bend Type","Bend Section Up, Down, N/A","Bend Section Angle (elbow / degrees)","Bend      Section     Radius (in.)","tension (lbs.)","sidewall pres.       (lbs.)","tension (lbs.)","sidewall pres.  (lbs.)","sidewall pres.            (lbs.)","sidewall pres.            (lbs.)"]
[1,90,"UP",6,"VCDN","UP",90,"STD",69,44,109,71,35,55]
[2,null,"HZTL",10,"HZTL","N/A",60,"STD",94,61,216,140,47,105]
[3,null,"HZTL",1,"HZTL","N/A",60,"STD",117,76,365,237,58,176]
[4,null,"HZTL",250,"HZTL","N/A",90,"STD",441,286,1908,1236,184,789]
[5,null,"HZTL",90,"VCUP","UP",90,"STD",707,455,4522,2931,288,1850]
[6,90,"UP",15,"VCDN","UP",90,"STD",1041,675,9900,6417,425,4044]
[7,null,"HZTL",106,"HZTL","N/A",90,18,1536,785,21850,11164,491,7021]
[8,null,"HZTL",35,"VCDN","Down",90,24,2130,797,47334,17718,498,11138]
[9,90,"Down",20,{"$nulls":4},2040,797,47249,17718,498,11138]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[null,null,"Total Feet",533,{"$nulls":6},"Comparison 1",null,"Comparison 2","Comparison 3"]
[{"$nulls":7},"Desired Ampacity:","1200 amps ",null,"1200 amps ",null,"1200 amps","1200 amps"]
[{"$nulls":7},"Configuration:","4 sets of 3/C 350 & 4/0 GW",null,"4 sets of 3/C 350 & 4/0 GW",null,"4 sets of 500 & 350 GW","4 sets of 500 & 350 GW"]
[{"$nulls":7},"Conduit:","3\" Galv Rigid (23% fill)",null,"3\" Galv Rigid (23% fill)",null,"3\" Galv Rigid (30% fill)","3\" Galv Rigid (30% fill)"]
[{"$nulls":7},"Maximum pulling force:","8074 lb.",null,"8074 lb.",null,8880,8880]
[{"$nulls":7},"Maximum sidewall pressure:","1000 lb.",null,"500 lb.",null,"1000 lb.","500 lb."]
[{"$nulls":7},"Short Circuit Current @ 8 cycles:","50,712 amps",null,"50,712 amps",null,"47, 384 amps","64,365 amps"]
[]
[]
[null,null,null,"Conduit system is assumed to be clean and free of debris."]
[]
[]
[]
[]
[]
[]
["Southwire Engineering  conservative Coefficient Of Friction (COF)  "]
[null,".35 for regular THHN THWN, XHHW and USE that requires lube "]
[null,".16 for SIMpull XHHW that requires no lube"]
[null,".14 for SIMpull THHN THWN that requires no lube"]

{"sheet":"Form for a cable pull calc","index":4,"n_rows":32,"n_cols":28,"rows_kept":32,"cut":false,"hidden":true,"merged":[[1,8,5,20],[20,0,22,1],[23,0,24,1],[18,3,18,27]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":8},"Straight Line Drawing for calculating a cable pull"]
[]
[]
[]
[]
[]
[null,null,"Purple Areas = Input is mandatory for doing a cable pull calculation."]
[]
[]
[null,null,"What wire are you pulling into your raceway: number of wires, size and metal type, Insulation type, GW same info."]
[{"$nulls":8},"(Example: 4/C 350 CU SIMpull THHN & 1 /C of 1/0 CU THHN GW)"]
[{"$nulls":8},"(Example: 1/C 350 CU 420 mil 35kV with a SIMpull PVC Jkt)"]
[]
[null,null,"What type and size of Raceway are you using.  If using PVC indentify if it is schedule 40 or schedule 80. (Example: 3\" Sch 40)"]
[{"$nulls":7},"      If using Cable Tray you will need to know your radius (inches) of bend sections.  "]
[]
[]
[null,null,null,"Segment # (Reel set-up to the end of the 1st bend is segment # 1, segment 2 goes from the end of # 1 to the end of the 2nd bend, and on to the end of the pull.)"]
[null,null,"Pull #1",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
["Straight Section",null,"Angle / (slope) of the pull"]
[null,null,"Direction Wire is being pulled :         (Up, Down, Hztl)"]
[null,null,"Length (Ft.) through the end of elbow"]
["Bend Section",null,"Degree of Elbow / bend"]
[null,null,"Radius (in.)             (Standard or Other)"]
[]
[]
[null,null,"Yellow = input is optional, but assumed to be ... "]
[]
[null,null,"Angel / (slope)  automatically populates as 90 degrees when you select \"up\" or \"down\". Or you can select other degrees if you wish. "]
[]
[null,null,"Radius of Elbow or bend automatically populates as \"standard\".  Or you can select specific sweeps or enter a unique bend raduis if you wish. "]

{"sheet":"Calc for 600V","index":5,"n_rows":64,"n_cols":27,"rows_kept":64,"cut":false,"hidden":false,"merged":[[62,14,62,15],[58,14,58,16],[59,14,59,15],[60,14,60,15],[61,14,61,15],[12,0,13,1],[56,11,56,12],[58,9,58,10],[19,3,19,4],[56,0,56,9],[38,11,39,16],[56,14,56,16],[31,12,31,13],[30,12,30,13],[13,7,13,10],[0,11,0,13],[1,11,1,13],[33,1,33,3],[22,0,23,13],[16,10,17,10],[29,12,29,13],[21,4,21,9],[18,11,18,12],[15,0,15,4],[18,7,18,9],[4,0,4,5],[33,10,34,10],[33,4,33,7],[0,9,0,10],[0,7,1,8]],"flags":["formulas_cached_only"]}
[null,"1",null,"Copyright Southwire Company 2009.    ",null,null,null,"Enter Voltage Drop Info in purple areas",null,"SIMpull CU THHN",null,"Phase Wire Attributes",{"$nulls":14},1]
[null,"1",null,"Tutorial link (36 minutes):",{"$nulls":5},"Single Phase","Three Phase","Attributes can change based on wire type, size and Mfg",{"$nulls":14},1]
[null,null,null,"https://www.youtube.com/embed/GCTYGnLVA6c",{"$nulls":4},"Amperage @ load (one set )",0,0,null,"Acceptable Megohm Readings",0,{"$nulls":12},1]
[null,null,null,"For more information, go to Southwire.com ",{"$nulls":4},"System Voltage",120,480,null,"Dielectric Constant ",0,{"$nulls":12},1]
["Enter wire info in purple areas that will go into the raceway",{"$nulls":7},"Circuit Length",0,0,null,"Max Oper Temp for Dry Use",0,{"$nulls":12},1]
[null,"# of wires","Wire Type","Wire Size","Wire OD","Wire Wt/ ft.",null,null,"Voltage Drop % (NEC Tbl 9)",0,0,null,"Max Oper Temp for Wet Use",0,{"$nulls":12},1]
["Phase Wires",null,1,1,0,0,null,null,"Volts at Load",120,480,null,"Min Bend Radius (in.)",0,{"$nulls":12},1]
["Neutral Wire",null,1,1,0,0,null,"Power Factor for Voltage Drop ",{"$nulls":4},"Min Installation Temp",0,{"$nulls":12},1]
["Ground Wire",null,1,1,0,0,null,null,"is:",0.8,null,null,"Vertically Support every ",0,{"$nulls":12},1]
["Total Cables",0,"Sets","Reel Size (D X W)","Feet","Gross Wt.",null,"Cable Pull Calculated  Values",null,null,null,"Riser MC Requires No Vertical Supports",{"$nulls":14},1]
[null,"",1,"C17 (34\" X 27.5\")",0,164.75,null,null,"Maximum Pulling Force (lb.)",0,null,null,"Sunlight Resistant",0,{"$nulls":12},1]
[{"$nulls":8},"Max Sidewall Pres. (lb.)",0,null,null,"CT Rated",0,{"$nulls":12},1]
["Equipment GW  (NEC 250.122) w/o VD considerations to OCD",null,15,"     CU  4/0 CU",{"$nulls":4},"Jam Probability",0,"Very Small",null,"UL",0,{"$nulls":12},1]
[null,null,null,"     AL  350 AL",null,null,null,"Phase Wire Ampacity Considerations ",{"$nulls":4},"NEMA",0,{"$nulls":12},1]
[{"$nulls":8},"Insulation Withstand Limit (a)",4,0,null,"RoHS Compliant",0,{"$nulls":12},1]
["Enter raceway info in purple areas",{"$nulls":7},"Adjust for Ambient Temp",2,0,null,"75 C Ampacity 310.15(B)(16)",0,{"$nulls":12},1]
["Raceway Type","1","",{"$nulls":4},"Adjust for # of Current",null,1,0,null," 90 C ampacity 310.15(B)(16)",0,{"$nulls":12},1]
["Raceway Size",2,"Min Conduit ","0.5 in. Per NEC",null,null,null,"Carrying Conductors",{"$nulls":4},"Coefficient Of Friction",0,{"$nulls":12},1]
["Conduit ID",0.622,"Maxis Size Grip","Min size conduit using 4 grips & jacket",null,null,null,"Max Allowable Ampacity for this Scenario           2017 NEC 310.15 (B) (16)",null,null,0,0,null,"Stranding"]
["% Conduit Fill",0,"","",{"$nulls":8},"All rights reserved.  See terms and conditions."]
[]
[{"$nulls":4},"Copy this url address to get Southwire's most current calc =",{"$nulls":5},"https://www.southwire.com/calculator-simpull"]
["SIMpull Cable Pull Calculator for 600V 5.13"]
[]
["Yellow areas = you have the ability to change data."]
["Purple areas = input required.",null,"0' of "]
[null,null,"0.5\" EMT "]
["Total wt./ ft",0]
["Configuration","4",null,null,"Maximum Pulling Force (lb.)",0]
["Wt.correction factor",1.4,null,null,"Max Sidewall Pres. (lb.)",0,null,null,"COF 0",null,null,"Feeder:"]
["COF",0,null,null,"Jam Probability","Very Small",null,null,"Recommended",null,null,"Origin:"]
["Incoming tension","25",{"$nulls":6},"SIMpull CU THHN",null,null,"Destination:"]
[{"$nulls":8},"No Lube Required"]
[null,"Straight Section",null,null,"Bend Section ",null,null,null,"Colored wires",null,"Begin new pull in this segment","Notes:"]
["Wire pull / Segment","Angle    (Slope)","Wire is being pulled …","Segment Length ft.","Bend Type","Up, Down, N/A","Degree of elbow","Radius (in.)","continuous tension (lbs.)","sidewall pressure    (lbs.)"]
[1,1,4,null,"","",1,1,0,0]
[2,1,4,null,"","",1,1,0,0]
[3,1,4,null,"","",1,1,0,0]
[4,1,4,null,"","",1,1,0,0,null,"Southwire recommended wire pulling equipment."]
[5,1,4,null,"","",1,1,0,0]
[6,1,4,null,"","",1,1,0,0,null,"1.  Southwire factory installed SIMpull Heads for pre-cut paralleled reels"]
[7,1,4,null,"","",1,1,0,0]
[8,1,4,null,"","",1,1,0,0,null,"2.  Minumum size cable puller and a 9/16 SIMpull Rope."]
[9,1,4,null,"","",1,1,0,0]
[10,1,4,null,"","",1,1,0,0,null,"         Maxis 3K has a maximum pulling force of 3,000 lb. and pulls"]
[11,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 1,500lb.   Use a  9/16' SIMpull Rope."]
[12,1,4,null,"","",1,1,0,0]
[13,1,4,null,"","",1,1,0,0,null,"         Maxis 6K has a  maximum pulling force of 6,000 lb. and pulls"]
[14,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 3,500lb.   Use a 9/16\" SIMpull Rope."]
[15,1,4,null,"","",1,1,0,0]
[16,1,4,null,"","",1,1,0,0,null,"         Maxis  XD 10K has a maximum pulling force of 10,000 lb. and pulls"]
[17,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 7,000lb.   Use a 9/16\" SIMpull Rope."]
[18,1,4,null,"Call Southwire if you neeed additional segments",null,null,null,0,0,null,"http://www.southwiretools.com/"]
[null,null,"Total  Length   ",0]
[]
[]
["Conduit system is assumed to be clean and free of debris.",{"$nulls":10},"Unique Bend Radius",null,"Unique Bend Degree","Unique Angle (Slope)"]
[{"$nulls":10},{"$error":"#DIV/0!"}]
["Southwire Engineering  conservative Coefficient Of Friction (COF)  ",{"$nulls":8},"Determines Unique Bend Radius",null,null,"enter as FEET","Enter as Degree","Enter as degree(s)"]
[null,".35 for regular THHN THWN, XHHW and USE; all requiring lube as recommended ",{"$nulls":7},"Degree of bend",0,"UBR # 1 =",0,0,"Angle # 1 =",null,0]
[null,".16 for SIMpull XHHW that requires no lube",{"$nulls":7},"Distance of bend (Ft.)",0,"UBR # 2 =",0,0,"Angle # 2 =",null,0]
[null,".14 for SIMpull THHN THWN that requires no lube",{"$nulls":7},"Bend Radius (Ft.) is  =",0,"UBR # 3 =",0,0,"Angle # 3 =",null,0]
[{"$nulls":11},"UBR # 4 =",0,0,"Angle # 4 =",null,0]
["Note: Rollers or sheaves are found in drop down of \"Radius (in.)\"  Example; a 12\" diameter roller is 6\" RR\" (radius roller)"]

{"sheet":"VoP","index":6,"n_rows":1,"n_cols":1,"rows_kept":1,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["Info as of 11-1-16, Dave Watson"]

{"sheet":"600V Cable Pull Comparison","index":7,"n_rows":87,"n_cols":23,"rows_kept":87,"cut":false,"hidden":true,"merged":[[35,8,35,9],[35,10,35,11],[40,3,43,11],[36,8,36,9],[36,10,36,11],[37,8,37,9],[37,10,37,11],[34,8,34,9],[34,10,34,11],[4,0,5,13],[31,10,31,11],[32,8,32,9],[32,10,32,11],[33,8,33,9],[33,10,33,11]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":4},"0' of "]
[{"$nulls":6},"0.5\" EMT "]
[]
["SIMpull Cable Pull Comparison using different Conductors"]
[]
["Total wt./ ft",0]
["Configuration","COMPLEX",{"$nulls":6},"COF 0",null,"COF .35",null,"COF .14","COF .35"]
["Wt.correction factor",1.4,{"$nulls":6},"Recommended",null,"Not Recommended",null,"Recommended","Not Recommended"]
["COF",0,{"$nulls":6},"SIMpull CU THHN",null,"CU THHN",null,"SIMpull AL THHN","AL XHHW"]
["Incoming tension","25",{"$nulls":6},"No Lube Required",null,"Lube Required",null,"No Lube Required","Lube Required"]
[{"$nulls":8},"Colored Wires",null,"Black with phase tape",null,"Colored Wires","Black with phase tape",null,null,"Maximum Pulling Force (lb.)",0,0,0,0]
["Wire pull / Segment","Straight Section Angle (slope / degrees)","Wire is being pulled ..","Segment Length Ft.","Bend Section Bend Type","Bend Section Up, Down, N/A","Bend Section Angle (elbow / degrees)","Bend      Section     Radius (in.)","tension    (lbs.)","sidewall pres.       (lbs.)","tension   (lbs.)","sidewall pres.  (lbs.)","sidewall pres.            (lbs.)","sidewall pres.            (lbs.)",null,null,"Max Sidewall Pres. (lb.)",0,500,0,0]
[1,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[2,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[3,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[4,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[5,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[6,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[7,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[8,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[9,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[10,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[11,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[12,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[13,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[14,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[15,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[16,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[17,"","","","","","","","","","","","","",null,null,null,0,0,0,0,0,0]
[18,"","","","","",0,{"$error":"#VALUE!"},"","","","","","",null,null,null,0,0,0,0,0,0]
[null,null,"Total Feet",0,{"$nulls":6},"Comparison 1",null,"Comparison 2","Comparison 3"]
[]
[{"$nulls":7},"Configuration:","/C 0 & 0 GW",null,"/C 0 & 0 GW",null,"/C 0 & 0 GW","/C 0 & 0 GW"]
[{"$nulls":7},"NEC Minumum SizeConduit:","0.5\" EMT (0% fill)",null,"0.5\" EMT (0% fill)",null,"0.5\" EMT (0% fill)","0.5\" EMT (0% fill)"]
[{"$nulls":7},"Maximum pulling force:","0 lb.",null,"0 lb.",null,"0 lb.","0 lb."]
[{"$nulls":7},"Maximum sidewall pressure:","0 lb.",null,"500 lb.",null,"0 lb.","0 lb."]
[{"$nulls":7},"Short Circuit Current @ 8 cycles:","0 amps",null,"0 amps",null,"0 amps","0 amps"]
[]
[]
[null,null,null,"Conduit system is assumed to be clean and free of debris."]
[]
[]
[]
[]
[]
[]
["Southwire Engineering  conservative Coefficient Of Friction (COF)  "]
[null,".35 for regular THHN THWN, XHHW and USE that requires lube "]
[null,".16 for SIMpull XHHW that requires no lube"]
[null,".14 for SIMpull THHN THWN that requires no lube"]
{"$rows_empty":18}
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]

{"sheet":"Terms and Conditions","index":8,"n_rows":24,"n_cols":1,"rows_kept":24,"cut":false,"hidden":true,"merged":[[23,0,27,9],[1,0,1,9],[3,0,9,9],[10,0,15,9],[16,0,20,9],[2,0,2,9]],"flags":["formulas_cached_only"]}
[]
["\"All-In-One\" estimating Tool & SIMpull® Cable Pull Calculator Terms and Conditions of Use"]
[]
["These spreadsheet calculation and estimation tools enable the user to perform basic calculation for cable tensions when pulled in conduit. Conduit system should be clean and free of debris. The tools use formulas and methods found in the public domain. These spreadsheet calculation and estimating tools are not intended to be, nor should it be, used as an authority for design, construction, use or installation of cable into conduit systems The design, construction, use and installation of cable into conduit systems should only be undertaken by competent professionals in accordance with currently accepted design and engineering practices."]
[]
[]
[]
[]
[]
[]
["While great care has been employed to ensure that the applications, tables, standards and references and other information contained herein are free of errors, absolutely no warranties, either expressed or implied, are made as to the accuracy or completeness of any such tables and formulas contained herein."]
[]
[]
[]
[]
[]
["THOSE PREPARING AND/OR CONTRIBUTING TO THE DEVELOPMENT OR USE OF THESE SPREADSHEET CALCULATION AND ESTIMATION TOOLS SPECIFICALLY DISCLAIM ANY WARRANTY OF ANY KIND, EITHER EXPRESSED OR IMPLIED. THE WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE HEREBY SPECIFICALLY DISCLAIMED BY SOUTHWIRE AND ALL OTHER PARTIES INVOLVED IN THE CREATION, PRODUCTION, OR DELIVERY OF THESE SPREADSHEET CALULATION AND ESTIMATION TOOLS."]
[]
[]
[]
[]
[]
[]
["Neither Southwire nor anyone else who has been involved in the creation, production or delivery of this publication shall be liable for any direct, indirect, consequential, or incidental damages arising out of the use, the results of the use, or inability to use such publication, even if Southwire has been advised of the possibility of such damages or claim. Some states do not allow the exclusion or limitation for consequential incidental damages, so the above limitation may not apply to you. "]

{"sheet":"Calc for Power Cable","index":9,"n_rows":86,"n_cols":27,"rows_kept":86,"cut":false,"hidden":false,"merged":[[0,13,0,16],[9,13,9,14],[1,13,1,14],[7,13,7,14],[8,13,8,14],[2,13,2,14],[3,13,3,14],[4,13,4,14],[14,15,16,16],[18,13,18,14],[29,12,29,14],[64,14,64,16],[20,13,20,14],[19,13,19,14],[63,11,64,13],[4,0,4,11],[5,4,6,5],[12,3,13,3],[5,6,6,7],[5,13,5,14],[6,13,6,14],[10,13,10,14],[12,0,13,1],[9,6,9,7],[10,6,10,7],[21,7,21,9],[17,13,17,14],[7,4,7,5],[7,6,7,7],[11,13,11,14],[12,6,15,10],[13,13,13,14],[14,13,16,14],[12,13,12,14],[59,4,59,7],[30,12,30,14],[31,12,31,14],[61,0,61,9],[15,0,15,4],[19,3,19,4],[32,8,32,9],[30,8,31,9],[22,0,23,16],[33,1,33,3],[33,4,33,7],[38,11,39,16],[33,10,34,10],[56,15,57,16],[58,15,58,16],[56,11,57,13]],"flags":["formulas_cached_only"]}
[null,"1",null,"Copyright Southwire Company 2009.    ",{"$nulls":9},"Phase wire / cable information",{"$nulls":12},1]
[null,"1",null,"All rights reserved.",{"$nulls":9},"Product Sheet (URL address)",null,"https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",{"$nulls":10},1]
[null,null,null,"See terms and conditions.",{"$nulls":9},"Southwire Product Type",null,"EFC CT1-13ET SIMpull PVC Jkt",{"$nulls":10},1]
[{"$nulls":13},"Southwire stock #",null,"95-60-45-99",{"$nulls":10},1]
["Enter wire info in purple areas that will go into the raceway",{"$nulls":12},"GW in the cable",null,"N/A",{"$nulls":10},1]
[{"$nulls":4},"Cable                Conductor Count",null,"Voltage/ Ins Level / Shield",{"$nulls":6},"NEC Ampacity Tables ",null,"AMPS",{"$nulls":10},1]
[null,"# of cables","Wire Size","CU or AL",{"$nulls":4},"Armor","Jacket","OD","WT/ Ft.",null,"Duct 310.60(C)(77) @ 90 C",null,465,{"$nulls":10},1]
[" Phase Conductor",null,"16",1,1,null,8,null,1,3,1.505,2.317,null,"Duct 310.60(C)(77) @ 105 C",null,500,{"$nulls":10},1]
["Ground Wire",null,1,1,{"$nulls":6},0,0,null,"CT Rated ",null,"Yes ",{"$nulls":10},1]
["Total Cables",0,null,null,"Sets","Feet","Reel Size (D X W) inches",null," Gross Wt. Lb.",{"$nulls":4},"Maximum reel length (feet)",null,3000,{"$nulls":10},1]
[{"$nulls":4},1,0,"",null,164.75,"",null,null,null,"Reel Size = Diameter X Width (inches)",null,"72 x 42",{"$nulls":10},1]
[{"$nulls":13},"Approx. gross wt (lb.) for max length",null,7507.080000000002,{"$nulls":10},1]
["Equipment GW (NEC 250.122) w/o VD considerations",null,15,"     CU  4/0 CU",null,null,"You can possibly eliminate splices and vaults when ordering wire with a SIMpull PVC Jacket and No Lube will be necessary for installation.  Use a COF of .20 SIMpull PVC Jacket in conduit",{"$nulls":6},"Conductor Short Circuit Rating (Amps)",null,185770.85565505372,2,{"$nulls":9},1]
[{"$nulls":13},"Shield Short Circuit Rating (Amps)",null,7386.994496254054,"for 0.0333 sec",{"$nulls":9},1]
[{"$nulls":13},"High Potential Testing per Table 4 of IEEE standard 400",null,"System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",{"$nulls":10},1]
["Enter raceway info in purple areas",{"$nulls":25},1]
["Raceway Type","1","",{"$nulls":23},1]
["Raceway Size",2,"Min Conduit ","0.5 in. Per NEC",{"$nulls":9},"Min bend radius of cable (inches)",null,18.06,{"$nulls":10},1]
["Conduit ID",0.622,{"$nulls":11},"Coefficient of Friction (COF) in conduit",null,0.2,{"$nulls":10},1]
["% Conduit Fill",0,{"$nulls":11},"Min installation temp",null,"-10C (14F)",{"$nulls":10},1]
[{"$nulls":26},1]
[{"$nulls":26},1]
["SIMpull Cable Pull Calculator for Power Cable 5.13",{"$nulls":25},1]
[{"$nulls":26},1]
["Yellow areas = you have the ability to change data.",{"$nulls":25},1]
["Purple areas = input required.",{"$nulls":8},"0' of 0 cable(s) 500 CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[{"$nulls":7},"0.5\" EMT "]
["Total wt./ ft",0]
["Configuration","4",null,null,"Maximum Pulling Force (lb.)",0]
["Wt.correction factor",1.4,null,null,"Max Sidewall Pres. (lb.)",1000,null,null,"COF 0.2",null,null,"Feeder:"]
["COF",0.2,null,null,"Jam Probability","Very Small",null,null,"Recommended",null,null,"Origin:"]
["Incoming tension","25",{"$nulls":9},"Destination:"]
[]
[null,"Straight Section",null,null,"Bend Section ",{"$nulls":5},"Begin new pull in this segment","Notes"]
["Wire pull / Segment","Angle    (Slope)","Wire is being pulled …","Segment Length ft.","Bend Type","Up, Down, N/A","Degree of elbow","Radius       (in.)","Continuous Tensions    (lb.)","Sidewall Pressure    (lb.)"]
[1,1,4,null,"","",1,1,0,0]
[2,1,4,null,"","",1,1,0,0]
[3,1,4,null,"","",1,1,0,0]
[4,1,4,null,"","",1,1,0,0,null,"Southwire recommended wire pulling equipment."]
[5,1,4,null,"","",1,1,0,0]
[6,1,4,null,"","",1,1,0,0,null,"1.  Southwire factory installed SIMpull Heads for pre-cut paralleled reels"]
[7,1,4,null,"","",1,1,0,0]
[8,1,4,null,"","",1,1,0,0,null,"2.  Minumum size cable puller and a 9/16 SIMpull Rope."]
[9,1,4,null,"","",1,1,0,0]
[10,1,4,null,"","",1,1,0,0,null,"         Maxis 3K has a maximum pulling force of 3,000 lb. and pulls"]
[11,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 1,500lb.     Use a 9/16' SIMpull Rope."]
[12,1,4,null,"","",1,1,0,0]
[13,1,4,null,"","",1,1,0,0,null,"         Maxis 6K has a maximium pulling force of 6,000 lb. and pulls"]
[14,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 3,500lb.      Use a 9/16\" SIMpull Rope."]
[15,1,4,null,"","",1,1,0,0]
[16,1,4,null,"","",1,1,0,0,null,"         Maxis XD 10K has a maximium pulling force of 10,000 lb. and pulls"]
[17,1,4,null,"","",1,1,0,0,null,"Continuous","Tensions up to 7,000lb.      Use a 9/16\" SIMpull Rope."]
[18,1,4,null,"","",1,1,0,0,null,"http://www.southwiretools.com/"]
[19,1,4,null,"","",1,1,0,0]
[20,1,4,null,"","",1,1,0,0]
[21,1,4,null,"","",1,1,0,0]
[22,1,4,null,"","",1,1,0,0,null,"Unique Bend Radius",null,null,null,"Unique Degree of Bend"]
[23,1,4,null,"","",1,1,0,0]
[24,1,4,null,"","",1,1,0,0,null,null,"enter as feet",null,null,"enter as degree of bend"]
[25,1,4,null,"Call Southwire if more segments are needed.",null,null,null,0,0,null,"UBR # 1 =",0,null,null,"Degree =",0]
[null,null,"Total Length",0,{"$nulls":7},"UBR # 2 =",0,null,null,"Degree =",0]
["Conduit system is assumed to be clean and free of debris.",{"$nulls":10},"UBR # 3 =",0,null,null,"Degree =",0]
[{"$nulls":11},"UBR # 4 =",0,null,null,"Degree =",0]
["Note: Rollers or sheaves are found in drop down of \"Radius (in.)\"  Example; a 12\" diameter roller is 6\" RR  (radius roller)",{"$nulls":10},"Unique Angle (Slope)     enter as degree of angle"]
[{"$nulls":14},"Determines Unique Bend Radius"]
[{"$nulls":11},"Angle # 1 =",0,null,null,"Degree of bend =",0]
[{"$nulls":11},"Angle # 2 =",0,null,null,"Distance (Ft.) of bend =",0]
[{"$nulls":11},"Angle # 3 =",0,null,null,"Unique Bend Radius (Ft.) is  =",0]
[{"$nulls":10},"darby","Angle # 4 =",0,null,null,null,{"$error":"#DIV/0!"}]
{"$rows_empty":9}
["Jam Prob numeric value"]
[0.41328903654485055]
[]
["Max pulling force value"]
[0]
[]
["Max SWP Value"]
[1000]

{"sheet":"Power Cable Pull Comparison","index":10,"n_rows":94,"n_cols":25,"rows_kept":94,"cut":false,"hidden":true,"merged":[[41,12,44,13],[38,8,38,9],[39,12,39,13],[38,10,38,11],[4,0,5,13],[9,10,9,11],[9,12,9,13],[10,8,10,9],[10,10,10,11],[10,12,10,13],[11,12,11,13],[11,8,11,9],[11,10,11,11],[39,8,39,9],[39,10,39,11],[47,3,50,11],[40,8,40,9],[40,10,40,11],[41,8,41,9],[41,10,41,11],[44,8,44,9],[44,10,44,11],[43,8,43,9],[43,10,43,11],[42,8,42,9],[42,10,42,11]],"flags":["formulas_cached_only"]}
[{"$nulls":24},"                                               "]
[{"$nulls":4},"0' of 0 cable(s) 500 CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[{"$nulls":6},"0.5\" EMT "]
[]
["SIMpull Cable Pull Comparison using different Conductors of 1/C MV ONLY"]
[]
[]
["Configuration","COMPLEX",{"$nulls":6},"COF 0.2",null,"COF .35",null,"COF .20"]
["Wt.correction factor",1.4,{"$nulls":6},"Recommended",null,"Not Recommended",null,"Highly Recommended"]
["COF for SIMpull",{"$nulls":7},"1 / C 500 CU",null,"1 / C 500 CU",null,"1 / C 750 Aluminum"]
["Incoming tension","25",{"$nulls":6},"with SIMpull  Jkt",null,"with standard PVC Jkt",null,"with SIMpull  Jkt"]
[{"$nulls":8},"No Lube needed ",null,"Lube required",null,"No Lube needed",null,null,null,"Maximum Pulling Force (lb.)",0,0]
["Wire pull / Segment","Straight Section Angle (slope / degrees)","Wire is being pulled ..","Segment Length Ft.","Bend Section Bend Type","Bend Section Up, Down, N/A","Bend Section Angle (elbow / degrees)","Bend      Section     Radius (in.)","tension    (lbs.)","sidewall pres.       (lbs.)","tension    (lbs.)","sidewall pres.  (lbs.)","tension (lbs.)","sidewall pres.  (lbs.)",null,null,"Max Sidewall Pres. (lb.)",1000,1000,1000]
[1,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[2,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[3,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[4,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[5,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[6,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[7,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[8,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[9,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[10,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[11,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[12,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[13,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[14,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[15,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[16,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[17,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[18,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[19,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[20,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[21,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[22,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[23,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[24,"","","","","","","",0,0,"","","","",null,null,null,1,1,0,0,0,0]
[25,"","","","","",{"$error":"#VALUE!"},{"$error":"#VALUE!"},0,0,"","","","",null,null,null,1,1,0,0,0,0]
[null,null,"Total Feet",0,{"$nulls":4},"Comparison 1",null,"Comparison 2",null,"Comparison 3"]
[]
[{"$nulls":7},"Maximium pulling tension (lb.)",0,null,0,null,0]
[{"$nulls":12},"Note:  You may need a different AL size conductor than what has been selected above.  The values above are based on the same size conduit you chose for option # 1, which may be too small per NEC for this Al size conductor. "]
[]
[{"$nulls":6},"         "]
[]
[]
[]
[null,null,null,"Conduit system is assumed to be clean and free of debris."]
[]
[]
[]
[]
[]
[]
["Southwire Engineering  conservative Coefficient Of Friction (COF)  "]
[null,".35 for regular PVC that requires lube "]
[null,".20 for SIMpull PVC that requires no lube"]
{"$rows_empty":12}
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]
[1]

{"sheet":"NEC GW 250.66","index":11,"n_rows":20,"n_cols":7,"rows_kept":20,"cut":false,"hidden":true,"merged":[[3,2,4,6],[5,2,8,3],[5,5,8,6],[10,3,11,3],[10,6,11,6]],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,null,"NEC GW Table 250.66"]
[]
[null,null,"Size of Largest Ungrounded Service Entrance Conductor or Equivalent Area for Parallel Conductors (AWG/kcmil)",null,null,"Size of Grounding Electrode Conductor (AWG/kcmil)"]
[]
[]
[]
[]
[null,null,null,"Aluminum or Copper-Clad Aluminum",null,null,"Aluminum or Copper-Clad Aluminum"]
[null,null,"Copper",null,null,"Copper"]
[]
[null,null,"2 or smaller","1/0 or smaller",null,8,6]
[null,null,"1 or 1/0","2/0 -3/0",null,6,4]
[null,null,"2/0 or 3/0","4/0 -250",null,4,2]
[null,null,"over 3/0 -350","over 250-500",null,2,"1/0"]
[null,null,"over 350 - 600","over 500 - 900",null,"1/0","3/0"]
[null,null,"over 600 -1100","over 900 - 1750",null,"2/0","4/0"]
[null,null,"over 1100","over 1750",null,"3/0","250"]

{"sheet":" Sketch for 600V wire","index":12,"n_rows":125,"n_cols":255,"rows_kept":125,"cut":false,"hidden":true,"merged":[[11,22,11,25],[35,2,36,4],[6,11,6,14],[7,11,7,15],[8,11,8,15],[9,11,9,15],[10,18,10,21]],"flags":["formulas_cached_only"]}
[]
[null,null,null,"CO Logo goes here",{"$nulls":7},"Company name, etc.  goes here",{"$nulls":16},"Project name goes here"]
[]
[]
[]
[{"$nulls":8},"Cable Pull Calculations",{"$nulls":22},"Feeder Number:",null,0]
[{"$nulls":9},"#/C",null,"Wire  Size",{"$nulls":19},"Origin:",null,0,{"$nulls":9},"(Feet) - (Degree of elbow or bend)"]
[{"$nulls":8},"Phase wire",0,null,0,{"$nulls":19},"Destination:",null,0,{"$nulls":9},"Arrow pointing up is pulling up"]
[{"$nulls":8},"Neutral wire",0,null,0,{"$nulls":19},"Conduit Size:",null,"0.5\" EMT ",{"$nulls":9},"Arrow pointing down is pulling down"]
[{"$nulls":8},"Ground wire",0,null,0,{"$nulls":19},"Number of Sets:",null,1,{"$nulls":9},"Arrow pointing horizontal is pulling left or right through the bend"]
["This pull indicates a maximum tension (lb.) ",{"$nulls":17},0,{"$nulls":12},"Length in Feet:",null,0,{"$nulls":9},"Arrow indicates a change of direction (bend, kick, offset, etc.)"]
["This pull indicates a maximum sidewall pressure (lb.) ",{"$nulls":21},0,{"$nulls":19},"Not to scale."]
[{"$nulls":4}," "]
[{"$nulls":4}," ",{"$nulls":37},"Proper Maxis rope size is 9/16"]
[{"$nulls":4}," ",{"$nulls":37},"Proper Maxis tugger size is 3K"]
{"$rows_empty":22}
[{"$nulls":123},"60' - 0°"]
[]
[]
[]
[]
[{"$nulls":166},""]
[]
[]
[]
[]
[{"$nulls":210},""]
[]
[]
[]
[]
[{"$nulls":254},""]
{"$rows_empty":41}
[{"$nulls":81},""]
[]
[]
[{"$nulls":81},""]
[]
[{"$nulls":79},"",{"$nulls":6},""]
[]
[{"$nulls":81},""]
[{"$nulls":76},"",{"$nulls":9},""]
[{"$nulls":77},""]
[{"$nulls":75},"",null,null,"",null,null,"",null,null,"",{"$nulls":6},""]
[]
[]
[{"$nulls":81},""]
[{"$nulls":82},""]
[{"$nulls":80},"",null,null,"",null,null,""]
[]
[]
[]
[{"$nulls":87},""]
[{"$nulls":85},"",null,null,""]
[]
[]
[]
[]
[{"$nulls":90},""]
[]
[]
[]
[]
[{"$nulls":95},""]

{"sheet":"Sketch for Power Cable","index":13,"n_rows":160,"n_cols":255,"rows_kept":160,"cut":false,"hidden":true,"merged":[[11,21,11,24],[35,2,36,4],[6,12,6,15],[7,12,7,16],[8,12,8,16],[10,17,10,20]],"flags":["formulas_cached_only"]}
[]
[null,null,null,"CO Logo goes here",{"$nulls":7},"Company name, etc.  goes here",{"$nulls":16},"Project name goes here"]
[]
[]
[]
[{"$nulls":9},"Cable Pull Calculations",{"$nulls":21},"Feeder Number:",0]
[{"$nulls":10},"#/C",null,"Wire  Size",{"$nulls":18},"Origin:",0,{"$nulls":10},"(Feet) - (Degree of elbow or bend)"]
[{"$nulls":9},"Phase wire",0,null,"500",{"$nulls":18},"Destination:",0,{"$nulls":10},"Arrow pointing up is pulling up"]
[{"$nulls":9},"Ground wire",0,null,0,{"$nulls":18},"Conduit Size:","0.5\" EMT ",{"$nulls":10},"Arrow pointing down is pulling down"]
[{"$nulls":31},"Number of Sets:",1,{"$nulls":10},"Arrow pointing horizontal is pulling left or right through the bend"]
["This pull indicates a maximum tension (lb.) ",{"$nulls":16},0,{"$nulls":13},"Length in Feet:",0,{"$nulls":10},"Arrow indicates a change of direction (bend, kick, offset, etc.)"]
["This pull indicates a maximum sidewall pressure (lb.) ",{"$nulls":20},0,{"$nulls":21},"Not to scale."]
{"$rows_empty":25}
[{"$nulls":123},"60' - 0°"]
[]
[]
[]
[]
[{"$nulls":166},""]
[]
[]
[]
[]
[{"$nulls":210},""]
[]
[]
[]
[]
[{"$nulls":254},""]
{"$rows_empty":24}
[{"$nulls":79},""]
[]
[]
[]
[]
[{"$nulls":84},""]
[]
[]
[]
[]
[{"$nulls":89},""]
[]
[]
[]
[{"$nulls":83},""]
[{"$nulls":94},""]
[]
[{"$nulls":81},""]
[]
[{"$nulls":88},""]
[{"$nulls":99},""]
[]
[{"$nulls":79},"",{"$nulls":6},""]
[]
[{"$nulls":81},"",{"$nulls":11},""]
[{"$nulls":67},"",{"$nulls":5},"",null,null,"",{"$nulls":27},""]
[{"$nulls":77},""]
[{"$nulls":75},"",null,null,"",null,null,"",null,null,"",{"$nulls":6},""]
[]
[]
[{"$nulls":72},"",{"$nulls":5},"",null,null,""]
[{"$nulls":82},""]
[{"$nulls":80},"",null,null,"",null,null,"",{"$nulls":9},""]
[]
[]
[{"$nulls":77},"",{"$nulls":5},"",null,null,""]
[{"$nulls":87},""]
[{"$nulls":85},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":82},"",{"$nulls":5},"",null,null,""]
[{"$nulls":92},""]
[{"$nulls":90},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":87},"",{"$nulls":5},"",null,null,""]
[{"$nulls":97},""]
[{"$nulls":95},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":92},"",{"$nulls":5},"",null,null,""]
[{"$nulls":102},""]
[{"$nulls":100},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":97},"",{"$nulls":5},"",null,null,""]
[{"$nulls":107},""]
[{"$nulls":105},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":102},"",{"$nulls":5},"",null,null,""]
[{"$nulls":112},""]
[{"$nulls":110},"",null,null,"",{"$nulls":12},""]
[]
[]
[{"$nulls":107},"",{"$nulls":5},"",null,null,""]
[{"$nulls":117},""]
[{"$nulls":115},"",null,null,""]
[]
[]
[{"$nulls":112},"",{"$nulls":5},""]
[{"$nulls":122},""]
[{"$nulls":120},"",null,null,""]
[]
[]
[{"$nulls":117},"",{"$nulls":5},""]
[]
[{"$nulls":125},""]
[]
[]
[]
[]
[{"$nulls":130},""]

{"sheet":"Dropdown","index":14,"n_rows":227,"n_cols":77,"rows_kept":227,"cut":false,"hidden":true,"merged":[[115,1,115,2],[116,1,116,2],[117,1,117,2],[118,1,118,2],[44,12,45,15],[61,4,61,5],[102,6,102,8],[114,1,114,2],[191,0,192,0],[37,10,37,11],[38,10,38,11],[112,1,112,2],[113,1,113,2],[44,6,45,9],[108,5,108,6],[111,1,111,2],[106,4,106,6],[107,5,107,6],[149,0,149,10],[135,0,135,1],[175,0,176,0],[175,1,176,1],[175,2,176,2],[159,0,160,0],[159,1,160,1],[159,2,160,2],[161,4,161,5],[166,4,166,5],[127,0,127,1],[141,0,141,4],[136,0,136,1],[137,0,137,1],[138,0,138,1],[132,0,132,1],[133,0,133,1],[130,0,130,1],[131,0,131,1],[134,0,134,1],[159,3,160,3],[159,4,160,5],[191,1,192,1],[191,4,192,5],[162,4,162,5],[169,4,169,5],[163,4,163,5],[164,4,164,5],[165,4,165,5],[175,3,176,3],[188,4,188,5],[191,2,192,2],[191,3,192,3],[183,4,183,5],[184,4,184,5],[167,4,167,5],[168,4,168,5],[178,4,178,5],[170,7,170,9],[171,4,171,5],[172,4,172,5],[177,4,177,5],[175,4,176,5],[170,4,170,5],[211,2,213,2],[201,4,201,5],[202,4,202,5],[204,4,204,5],[203,4,203,5],[212,4,213,7],[200,4,200,5],[179,4,179,5],[180,4,180,5],[182,4,182,5],[198,4,198,5],[199,4,199,5],[186,4,186,5],[197,4,197,5],[181,4,181,5],[194,4,194,5],[196,4,196,5],[185,4,185,5],[193,4,193,5],[187,4,187,5]],"flags":["formulas_cached_only"]}
["Wire Type",null,"Wt. Cor Fct",null,null,"Coefficient",null,null,"Bend Type","Pull","Dir","Conduit",null,"Amps","AMPS","CU","AL",null,"Select","CU HV","AL HV","AL Conv",{"$nulls":5},"CU","AL-CU","CU-AL","AL",null,null,"CU","AL-CU","CU-AL","AL",null,"AL Wt.","AL Dia.","AL Cmil",null,null,"°","Angle",1,"Leg","Length","H","V","H","V",null,"R","C",0,null,"R","C",null,null,null,"Angle",1,"Leg","Length","H","V","H","V",null,"R","C",0,null,"R","C"]
["SIMpull CU THHN",null,"Single",null,null,"Metal","PVC",null,null,"HZTL","N/A","EMT",null,15,"       15 amps","14 CU","12 AL",{"$nulls":8},1,null,"N/A","N/A","N/A","N/A",null,1,"1",1,1,1,null,"N/A","N/A","N/A",null,null,null,"0°",1,4,"",35,235,{"$error":"#VALUE!"},{"$error":"#VALUE!"},40,5,5,0,10,2,2,null,null,null,"0°",1,4,"",35,235,{"$error":"#VALUE!"},{"$error":"#VALUE!"},40,5,5,0,10,2,2]
["SIMpull CU XHHW",null,"Triangular",null,"SIMpull THHN",0.14,0.14,null,"HZTL","UP","UP","PVC Sch 40 or HDPE",null,15,"       20 amps","12 CU","10 AL",null,"14 Str","14 Str","14 Str",{"$nulls":4},2,15,"14 Str","N/A","N/A","N/A",null,2,2,1,1,1,null,"N/A","N/A","N/A",null,null,null,"0°",2,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,11,0,3,null,null,null,"0°",2,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,11,0,3]
["CU USE",null,"Cradle",null,"XHHW",0.35,0.35,null,"VCUP","Down","Down","PVC Sch 80",null,null,"       30 amps","10 CU","8 AL",null,"12 Str","12 Str","12 Str",{"$nulls":4},3,20,"12 Str","N/A","N/A","N/A",null,3,3,1,1,1,null,"N/A","N/A","N/A",null,null,null,"0°",3,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,12,-1,2,null,null,null,"0°",3,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,12,-1,2]
["SIMPull AL THHN",null,"COMPLEX",null,"THHN",0.4,0.35,null,"VCDN",null,null,"Flex FMC",null,null,"       40 amps","10 CU","8 AL",null,"10 Str","10 Str","10 Str",{"$nulls":4},4,30,"10 Str","N/A","N/A","N/A",null,4,4,1,1,1,null,"N/A","N/A","N/A",null,null,null,"0°",4,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,13,2,2,null,null,null,"0°",4,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,13,2,2]
["SIMpull AL XHHW",{"$nulls":7},"Call SW!",null,null,"RMC (Galv or AL)",null,null,"       60 amps","10 CU","8 AL",null,"8","8","8",6,null,null,null,5,50,"8","N/A","6","N/A",50,5,5,1,6,1,null,"N/A","N/A","N/A",null,null,null,"0°",5,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,20,0,0,null,null,null,"0°",5,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,20,0,0]
["AL USE",{"$nulls":4},"R","C",null,"R","C",null,"Flex LFMC & LFNC-B",null,null,"       100 amps","8 CU","6 AL",null,6,6,6,4,null,null,null,6,65,"6","8","4","6",65,6,6,5,7,6,null,0.038,0.239,26240,null,null,null,"0°",6,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,21,-2,1,null,null,null,"0°",6,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,21,-2,1]
[{"$nulls":5},1,1,null,3,1,null,"RTRC IPS Fiberglass",null,null,"       200 amps","6 CU","4 AL",null,4,4,4,2,null,null,null,7,85,"4","6","2","4",90,7,7,6,8,7,null,0.062,0.305,41740,null,null,null,"0°",7,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,22,-3,0,null,null,null,"0°",7,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,22,-3,0]
[{"$nulls":11},"IMC",null,null,"       300 amps","4 CU","2 AL",null,2,2,2,1,null,null,null,8,115,"2","2","1/0","2",100,8,8,8,10,8,null,0.09,0.36,66360,null,null,null,"0°",8,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,23,5,5,null,null,null,"0°",8,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,23,5,5]
[null,null,"ECR",{"$nulls":8},"Cable Tray",null,null,"       400 amps","3 CU","1 AL",null,1,1,1,"1/0",null,null,null,9,130,"1","2","2/0","1",120,9,9,8,11,9,null,0.116,0.413,83690,null,null,null,"0°",9,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,30,3,0,null,null,null,"0°",9,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,30,3,0]
[{"$nulls":4},"PC","600V",{"$nulls":8},"       500 amps","2 CU","1/0 AL",null,"1/0","1/0","1/0","2/0",null,null,null,10,150,"1/0","1","3/0","1/0",135,10,10,9,12,10,null,0.141,0.45,105600,null,null,null,"0°",10,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,31,1,1,null,null,null,"0°",10,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,31,1,1]
[null,null,"Std",null,"Angle Slope","Angle Slope","Type of Insulation","Min Temp for Inst",null,null,"Bend Angle 600V","Bend Angle PC",null,null,"       600 amps","1 CU","2/0 AL",null,"2/0","2/0","2/0","3/0",null,null,null,11,175,"2/0","1/0","4/0","2/0",155,11,11,10,13,11,null,0.171,0.49,133100,null,null,null,"0°",11,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,32,5,5,null,null,null,"0°",11,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,32,5,5]
[null,null,12,null,null,null,"THHN","-10° C","14° F",{"$nulls":5},"       800 amps","1/0 CU","3/0 AL",null,"3/0","3/0","3/0","4/0",null,null,null,12,200,"3/0","2/0","250","3/0",180,12,12,11,14,12,null,0.21,0.537,167800,null,null,null,"0°",12,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,33,3,0,null,null,null,"0°",12,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,33,3,0]
[null,null,15,null,90,90,"XHHW","-40° C","-40° F",null,90,90,null,null,"      1000 amps","2/0 CU","4/0 AL",null,"4/0","4/0","4/0",250,null,null,null,13,230,"4/0","3/0","350","4/0",205,13,13,12,15,13,null,0.257,0.589,211600,null,null,null,"0°",13,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,40,5,5,null,null,null,"0°",13,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,40,5,5]
[null,null,18,null,45,45,{"$nulls":4},75,75,null,null,"      1200 amps","3/0 CU","250 AL ",null,250,250,250,"350",null,null,null,14,255,"250","4/0","350","250",250,14,14,13,15,14,null,0.257,0.589,211600,null,null,null,"0°",14,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,44,5,5,null,null,null,"0°",14,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,44,5,5]
[null,null,24,null,30,30,{"$nulls":8},"      1600 amps","4/0 CU","350 AL",null,"350","350","350","500",null,null,null,15,310,"350","250","500","350",310,15,15,14,16,15,null,0.417,0.752,350000,null,null,null,"0°",15,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,{"$nulls":6},"0°",15,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,30,null,22.5,22.5,{"$nulls":4},60,60,null,null,"     2000 amps","250 CU","400 AL",null,"500","500","500","600",null,null,null,16,380,"500","350","750","500",340,16,16,15,18,16,null,0.575,0.872,500000,null,null,null,"0°",16,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,{"$nulls":6},"0°",16,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,36,null,11.25,11.25,{"$nulls":4},55,55,null,null,"     2500 amps","350 CU","600 AL",null,"600","600","600","750",null,null,null,17,420,"600","500","1000","600",385,17,17,16,19,17,null,0.698,0.971,600000,null,null,null,"0°",17,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,{"$nulls":6},"0°",17,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,42,null,0,0,{"$nulls":4},50,50,null,null,"     3000 amps","400 CU","600 AL",null,"750","750","750","1000",null,null,null,18,475,"750","N/A","1000","750",445,18,18,1,19,18,null,0.855,1.066,750000,{"$nulls":4},18,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0,{"$nulls":6},"0°",18,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,48,null,0,0,{"$nulls":4},45,45,null,null,"     4000 amps","500 CU","750 AL",null,"1000","1000","1000",1250,null,null,null,19,545,"1000","N/A","N/A","1000",null,19,19,1,1,19,null,1.115,1.218,1000000,{"$nulls":21},"0°",19,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"3\" RR",null,0,0,{"$nulls":4},35,35,null,null,"     5000 amps","700 CU","1200 AL",null,1250,1250,1250,1500,null,null,null,20,null,"1250","N/A","N/A","1250",null,20,20,1,1,20,{"$nulls":10},"",{"$nulls":14},"0°",20,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"6\" RR",null,0,0,{"$nulls":4},30,30,null,null,"     6000 amps","800 CU","1200 AL",null,1500,1500,1500,{"$nulls":4},21,null,"1500","N/A","N/A","1500",null,21,21,1,1,21,{"$nulls":10},"",{"$nulls":14},"0°",21,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"9\" RR",{"$nulls":7},25,25,{"$nulls":35},"",{"$nulls":14},"0°",22,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"12\" RR",{"$nulls":7},22.5,22.5,null,null,"GW sizing","Table",250.122,{"$nulls":30},"",{"$nulls":14},"0°",23,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"UBR # 1",{"$nulls":7},20,20,{"$nulls":35},"",{"$nulls":14},"0°",24,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"UBR # 2",{"$nulls":7},15,15,{"$nulls":35},"",{"$nulls":14},"0°",25,4,"",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},44,5,5,0]
[null,null,"UBR # 3",{"$nulls":7},11.25,11.25]
[null,null,"UBR # 4",{"$nulls":7},10,10]
[{"$nulls":10},0,0]
["Dielectric constants or SIC (specific inductive capacitance) PCM 6-6",{"$nulls":5},"PCM 3-4",null,null,null,0,0,{"$nulls":34},"600 Beg",0,{"$nulls":16},"600 Beg",0]
["Material","Type","Range","600V","MV",null,"?",null,null,null,0,0,{"$nulls":33},1,0,0,{"$nulls":15},1,0,0]
["PVC","THHN","3.4 - 8.0",8,"NA",null,3.4,null,null,null,0,0,{"$nulls":33},2,0,0,{"$nulls":15},2,0,0]
["EPR",null,"2.5 - 3.5",3.5,2.9,{"$nulls":40},3,0,0,{"$nulls":15},3,0,0]
["PE",null,"2.5 - 2.6",2.6,"NA",{"$nulls":40},4,0,0,{"$nulls":15},4,0,0]
["XLPE","XHHW","2.3 - 6.0",5,2.4,null,5,{"$nulls":38},5,0,0,{"$nulls":15},5,0,0]
[{"$nulls":45},6,0,0,{"$nulls":15},6,0,0]
[{"$nulls":45},7,0,0,{"$nulls":15},7,0,0]
["Cable min bend radius PCM 7-4",null,null,"Suggested Max sidewall pressure",null,null,"COF is .15 for any cable installed in cable tray",null,null,null,"Tech 90 1kV min bend radius",null,"Over 600V Min Bend Radius",{"$nulls":32},8,0,0,{"$nulls":15},8,0,0]
["Cable OD","Factor",null,"SIMpull",null,1000,"Configuration is \"single\" for any cable installed in cable tray",null,null,null,"per Jeff Posey 2-25-10",null,"Single and multi conductor (NEC 300.34)",{"$nulls":32},9,0,0,{"$nulls":15},9,0,0]
["0 - 1.0",4,null,"THHN XHHW USE",null,500,"Per Paul White 12-9-09",null,null,null,"Cable OD","Factor","Nonshielded",null,8,{"$nulls":30},10,0,0,{"$nulls":15},10,0,0]
["1.001 - 2.0",5,null,"Tray Cable",null,500,{"$nulls":4},"0 - .75",10,"Shielded ",null,12,{"$nulls":30},11,0,0,{"$nulls":15},11,0,0]
["2.001 - 3.0",6,null,"Interlocked armor",null,500,"Cable min bend Radius for 600V Type MC (NEC 330.24)",null,null,null,".76 - 1.50",12,"Multiconductor",null,"12",{"$nulls":30},12,0,0,{"$nulls":15},12,0,0]
[null,null,null,"Armor-X",null,1000,"Interlocked Armor or CCW",7,null,null,"1.51 - up",15,null,null,7,{"$nulls":30},13,0,0,{"$nulls":15},13,0,0]
[null,null,null,"Any Jacket on MV ",null,1000,"Shielded conductors ","12 / 7",{"$nulls":37},14,0,0,{"$nulls":15},14,0,0]
[null,null,null,"Per Paul White 12-9-09",null,null,"12 times the invividual shielded conductor diameter or 7 times the cable OD, whichever is greater.",{"$nulls":5},"12 times the invividual shielded conductor diameter or 7 times the cable OD, whichever is greater.",{"$nulls":32},15,0,0,{"$nulls":15},15,0,0]
[{"$nulls":45},16,0,0,{"$nulls":15},16,0,0]
[{"$nulls":45},17,0,0,{"$nulls":15},17,0,0]
["Short Circuit AmpacityPCM 6-16 through 20",{"$nulls":44},18,0,0,{"$nulls":15},18,0,0]
["    1/2 cycle / .00835 sec.",null,0.00835,{"$nulls":60},19,0,0]
["     1 cycle / .0167 sec.",null,0.0167,null,"PCM 6-14",{"$nulls":58},20,0,0]
["     2 cycles / .0333 sec.",null,0.0333,{"$nulls":60},21,0,0]
["     4 cycles / .0667",null,0.0667,{"$nulls":60},22,0,0]
["     8 cycles / .1333 sec. ",null,0.1333,{"$nulls":60},23,0,0]
["     12 cycles / .2000 sec.",null,0.2,{"$nulls":60},24,0,0]
["     30 cycles / .5000 sec.",null,0.5,{"$nulls":60},25,0,0]
["     60 cycles / 1.0 sec.",null,1]
["     100 cycles / 1.667 sec.",null,1.667]
[]
[]
[]
[]
["Support in verticel raceway PCM 7-32",null,null,null,"Jam Ratio PCM 7-17"]
["wire size","AL","CU",null,"0-2.4","very small"]
["18 -8","100 ft.","100 ft.",null,"2.4 -2.5","small"]
["6 - 1/0","200 ft.","100 ft.",null,"2.5-2.6","moderate"]
["2/0 - 4/0","180 ft.","80 ft.",null,"2.6 -2.9","significant"]
["250 - 350","135 ft.","60 ft.",null,"2.9-3.0","moderate"]
["400 - 500","120 ft.","50 ft.",null,"3.0-3.2","small"]
["600 - 750","95 ft.","40 ft.",null,"3.2 -up","very small"]
["900 - 1000","85 ft","35 ft."]
[]
[]
[{"$nulls":6},"Conductor ",null,"XHHW"]
[{"$nulls":6},"Size",null,2875]
[null,"USE",{"$nulls":4},14,null,2430]
[null,"RHH",{"$nulls":4},12,null,2010]
[null,"RHW",{"$nulls":4},10,null,2095]
[{"$nulls":6},8,null,1730]
[50,0.73,0.56,null,null,null,6,null,1430]
[55,0.86,0.75,null,null,null,4]
[60,1,1,null,null,null,3,null,1170]
[65,1.17,1.34,null,null,null,2,null,1235]
[70,1.36,1.79,null,null,null,1,null,1105]
[75,1.59,2.4,null,null,null,"1/0",null,1000]
[80,1.86,3.21,null,null,null,"2/0",null,895]
[85,"n/a",4.3,null,null,null,"3/0",null,825]
[{"$nulls":6},"4/0",null,895]
[{"$nulls":6},"250",null,825]
[{"$nulls":6},"300",null,755]
[{"$nulls":6},"350",null,715]
[{"$nulls":6},"400",null,645]
[{"$nulls":6},500,null,715]
[{"$nulls":6},600,null,645]
[{"$nulls":6},750]
[{"$nulls":6},900,null,565]
[{"$nulls":6},1000]
["Acceptable Megger reading"]
["Per Dave Mercier Jan 2009"]
["use ","50 - infinity "]
[]
["Formula is: (cable length X Resistance X temperature factor) Divided by 1000"]
[]
["size","type","length / ft.","temp 65","resistance"]
[350,"THHN",300,1.34,240]
[]
[]
["Min installation temp PCM 7-2",null,null,null,"Minimum Operation Temp"]
["THHN","-10C (14F)",null,null,"THHN","-25C (-10 F) THHN"]
["XLP","-40C (-40F)",null,null,"XHHW","-40 C (-40F) XHHW"]
[]
["Number of current carrying conductors BWHB 100"]
["            conductors","Correction factor"]
["            1-3",1]
["            4-6",0.8]
["            7-9",0.7]
["            10-20",0.5]
["            21-30",0.45]
["            31-40",0.4]
["            41 up",0.35]
[]
["Max allowable conductor Stress  PCM 7-10",{"$nulls":5},"Conductor Short Circuit Factors, Fc"]
["CU /soft",0.008,"per cmil",null,null,null,"Insulation","Copper","Aluminum"]
["AL / 8000 ",0.006,"per cmil",null,null,null,"Thermoset (XLPE, ERP) 105 - 250",0.0678,0.0443]
["Max",10000,{"$nulls":4},"Thermoset (XLPE, ERP)  90-250",0.0719,0.047]
["Basket grips",1000,{"$nulls":4},"Thermoplastic (PVC, PE) 75 - 100",0.0529,0.0346]
[]
["Ambient Temp correction factors for CU and AL",null,null,null,"PCM 6-31"]
["Ambient Temp ",null,"60C","75C","90C"]
[]
[]
["     21-25C (70-75F)",null,1.08,1.05,1.04,null,"9/16",100000,"N/A","N/A"]
["     26-30C (78-86F)",null,1,1,1,null,"3K",8500,"7/8","10K"]
["     31-35C (87-95F)",null,0.91,0.94,0.96,null,null,4500,"5/8","6K"]
["     36-40C (96-104F)",null,0.82,0.88,0.91,null,0,2000,"9/16","3K"]
["     41-45C (105-113F)",null,0.71,0.82,0.87,null,0,0,"9/16","3K"]
["     51-55C (114-122F)",null,0.58,0.75,0.82]
["     56-60C (123-131F)",null,0.41,0.67,0.76]
["     61-70C (141-158F)",null,null,0.58,0.71]
["     71-80C (159-176F)",null,null,0.33,0.58]
[{"$nulls":4},0.41]
[{"$nulls":6},"9/16",100000,"N/A","N/A"]
["Stranding",{"$nulls":5},"3K",8500,"7/8","10K"]
["AL","Compact AA-8000 Series Alloy Class B",{"$nulls":5},4500,"5/8","6K"]
["CU","Compressed Soft CU Class B",{"$nulls":4},0,2000,"9/16","3K"]
[{"$nulls":6},0,0,"9/16","3K"]
[]
[]
[]
[]
["Important installation Instruction for Maxis Grips and Jacket"]
[]
["Just because the grips fit the wire does not mean the grips will fit into your conduit size.  "]
[]
["Use no more than four Maxis double locking grips on a pull, serve your GW or use the basket grip."]
[]
["When using the jacket you will probably need to remove the conduit insert part "]
["of the adapter before the jacket reaches the end of the pull."]
[]
[]
["SIMpull CU THHN","Maxis Size Grip","SIMpull AL THHN","Maxis Size Grip","Min size conduit using 4 grips & jacket"]
[]
["1/0","AA","2/0","AA"]
["2/0","AA","3/0","AA"]
["3/0","A","4/0","A",2]
["4/0","A",250,"A",2.5]
[250,"B","300","B",3]
["300","B","350","B",3]
["350","B","400","B",3]
["400","C","500","C",3]
["500","C","600","C",3.5]
["600","D","750","D",4,null,null,"Maxis Grip OD Range Per David "]
["750","D","900","D",4,null,null,"Size","Min Dia","Max Dia"]
[{"$nulls":7},"AA",0.474,0.624]
[{"$nulls":7},"A",0.568,0.673]
[{"$nulls":7},"B",0.678,0.809]
["SIMpull CU XHHW","Maxis Size Grip","AL XHHW","Maxis Size Grip","Min size conduit using 4 grips & jacket",null,null,"C",0.821,0.976]
[{"$nulls":7},"D",0.983,1.191]
["1/0","AA","2/0","AA"]
["2/0","AA","3/0","AA"]
["3/0","A","4/0","A",2]
["4/0","A",250,"A",2.5]
[250,"B","300","B",3]
["300","B","350","B",3]
["350","B","400","B",3]
["400","C","500","C",3]
["500","C","600","C",3.5]
["600","D","750","D",4]
["750","D","900","D",4]
[]
[]
[]
["CU USE","Maxis Size Grip","AL USE","Maxis Size Grip","Min size conduit using 4 grips & jacket"]
[]
["1/0","AA","2/0","AA"]
["2/0","AA","3/0","A"]
["3/0","A"]
["4/0","A","4/0","A",2]
[250,"B",250,"B",2.5]
["300","B","300","B",3]
["350","B","350","B",3]
["400","C","400","C",3]
["500","D","500","C",3]
["600","D",null,null,3.5]
["750","D","750","D",4]
[{"$nulls":4},4]
[]
[]
[]
[]
[]
["Power Cable Drop Downs"]
[null,null,"Cable Conductor Count"]
[{"$nulls":4},"Voltage / Ins Level / Shield"]
["CU or AL",{"$nulls":8},"Armor",null,"Jacket"]
["CU",null,"1 / C",null,null,null,"600V RHH RHW USE (XLP) ",null,null,"No",null,"No"]
["AL",null,"3 / C WG",null,null,null,"600V SIMpull XHHW ( XLP)",null,null,"Steel ",null,"PVC"]
[null,null,"4 / C WG",null,null,null,"600V THHN THWN",null,null,"Aluminum (AIA)",null,"SIMpull-PVC"]
[{"$nulls":6},"1kV Non Shielded",null,null,"Armor-X (CCA)",null,"CPE-PO"]
[{"$nulls":6},"2.4 kV Non Shielded",null,null,"Tech 90",null,"CPE-XLP"]
[{"$nulls":6},"5kV 115 Mil EPR 133% CU Tape",{"$nulls":4},"SOLONON PO"]
[{"$nulls":6},"15kV 175 Mil EPR 100% CU Tape",{"$nulls":4},"SOLONON XPL"]
[{"$nulls":6},"15kV 220 Mil EPR 133% CU Tape",{"$nulls":4},"SOLONON XLP"]
[{"$nulls":6},"25kV 320 MIL EPR 133% CU Tape"]
[{"$nulls":6},"28kV 280 MIL EPR 100% CU Tape"]
[{"$nulls":6},"35kV 345 MIL EPR 100% CU Tape"]
[{"$nulls":6},"35kV 420 Mil EPR 133% CU Tape"]
[{"$nulls":6},"2kV XLP  RHH / RHW-2 "]

{"sheet":"Supplied to BEM","index":15,"n_rows":182,"n_cols":27,"rows_kept":182,"cut":false,"hidden":true,"merged":[[156,6,158,6],[110,0,110,1],[111,0,111,1],[112,0,112,1],[115,0,115,4],[121,2,123,2],[122,4,123,7],[155,0,155,4],[156,2,158,2],[156,3,158,3],[156,4,158,4],[156,5,158,5],[109,0,109,1],[87,1,87,2],[88,1,88,2],[89,1,89,2],[90,1,90,2],[91,1,91,2],[101,0,101,1],[104,0,104,1],[105,0,105,1],[106,0,106,1],[107,0,107,1],[108,0,108,1],[86,1,86,2],[29,10,29,11],[30,10,30,11],[36,6,37,9],[36,12,37,15],[54,4,54,5],[75,6,75,8],[79,4,79,6],[80,5,80,6],[81,5,81,6],[84,1,84,2],[85,1,85,2]],"flags":["formulas_cached_only"]}
["NEC 2014",null,null,null,"CEC"]
["AMPS","CU","AL",null,"AMPS","CU","AL",null,"Raceway types",null,null,"Dielectric constants or SIC (specific inductive capacitance) PCM 6-6"]
["       15 amps","14 CU","12 AL",null,"       15 amps","14 CU","12 AL",null,"EMT",null,null,"Material","Type","Range","600V","MV"]
["       20 amps","12 CU","10 AL",null,"       20 amps","14 CU","12 AL",null,"PVC Sch 40 or HDPE",null,null,"PVC","THHN","3.4 - 8.0",8,"NA"]
["       30 amps","10 CU","8 AL",null,"       30 amps","12 CU","10 AL",null,"PVC Sch 80",null,null,"EPR",null,"2.5 - 3.5",3.5,2.9]
["       40 amps","10 CU","8 AL",null,"       40 amps","10 CU","8 AL",null,"Flex FMC",null,null,"PE",null,"2.5 - 2.6",2.6,"NA"]
["       60 amps","10 CU","8 AL",null,"       60 amps","10 CU","8 AL",null,"RMC (Galv or AL)",null,null,"XLPE","XHHW","2.3 - 6.0",5,2.4]
["       100 amps","8 CU","6 AL",null,"       100 amps","8 CU","6 AL",null,"Flex LFMC & LFNC-B"]
["       200 amps","6 CU","4 AL",null,"       200 amps","6 CU","4 AL",null,"RTRC IPS Fiberglass"]
["       300 amps","4 CU","2 AL",null,"       300 amps","4 CU","2 AL",null,"IMC"]
["       400 amps","3 CU","1 AL",null,"       400 amps","3 CU","1 AL",null,"Cable Tray"]
["       500 amps","2 CU","1/0 AL",null,"       500 amps","2 CU","1/0 AL"]
["       600 amps","1 CU","2/0 AL",null,"       600 amps","1 CU","2/0 AL"]
["       800 amps","1/0 CU","3/0 AL",null,"       800 amps","1/0 CU","3/0 AL"]
["      1000 amps","2/0 CU","4/0 AL",null,"      1000 amps","2/0 CU","4/0 AL "]
["      1200 amps","3/0 CU","250 AL ",null,"      1200 amps","3/0 CU","250 AL"]
["      1600 amps","4/0 CU","350 AL",null,"      1600 amps","4/0 CU","350 AL"]
["     2000 amps","250 CU","400 AL",null,"     2000 amps","250 CU","400 AL"]
["     2500 amps","350 CU","600 AL",null,"     2500 amps","350 CU","500 AL"]
["     3000 amps","400 CU","600 AL",null,"     3000 amps","400 CU","600 AL"]
["     4000 amps","500 CU","750 AL",null,"     4000 amps","500 CU","800 AL"]
["     5000 amps","700 CU","1200 AL",null,"     5000 amps","700 CU","1000 AL"]
["     6000 amps","800 CU","1200 AL",null,"     6000 amps","800 CU","1250 AL"]
[]
["GW sizing","Table",250.122,null,"GW sizing","Table",16]
[]
[]
[]
[]
["Cable min bend radius PCM 7-4",null,null,"Suggested Max sidewall pressure",null,null,"COF is .15 for any cable installed in cable tray",null,null,null,"Tech 90 1kV min bend radius",null,"Over 600V Min Bend Radius"]
["Cable OD","Factor",null,"SIMpull",null,1000,"Configuration is \"single\" for any cable installed in cable tray",null,null,null,"per Jeff Posey 2-25-10",null,"Single and multi conductor (NEC 300.34)"]
["0 - 1.0",4,null,"THHN XHHW USE",null,500,"Per Paul White 12-9-09",null,null,null,"Cable OD","Factor","Nonshielded",null,8]
["1.001 - 2.0",5,null,"Tray Cable",null,500,{"$nulls":4},"0 - .75",10,"Shielded ",null,12]
["2.001 - 3.0",6,null,"Interlocked armor",null,500,"Cable min bend Radius for 600V Type MC (NEC 330.24)",null,null,null,".76 - 1.50",12,"Multiconductor",null,"12"]
[null,null,null,"Armor-X",null,1000,"Interlocked Armor or CCW",7,null,null,"1.51 - up",15,null,null,7]
[null,null,null,"Any Jacket on MV ",null,1000,"Shielded conductors ","12 / 7"]
[null,null,null,"Per Paul White 12-9-09",null,null,"12 times the invividual shielded conductor diameter or 7 times the cable OD, whichever is greater.",{"$nulls":5},"12 times the invividual shielded conductor diameter or 7 times the cable OD, whichever is greater."]
[]
[]
[]
["Short Circuit AmpacityPCM 6-16 through 20"]
["    1/2 cycle / .00835 sec.",null,0.00835]
["     1 cycle / .0167 sec.",null,0.0167,null,"PCM 6-14"]
["     2 cycles / .0333 sec.",null,0.0333]
["     4 cycles / .0667",null,0.0667]
["     8 cycles / .1333 sec. ",null,0.1333]
["     12 cycles / .2000 sec.",null,0.2]
["     30 cycles / .5000 sec.",null,0.5]
["     60 cycles / 1.0 sec.",null,1]
["     100 cycles / 1.667 sec.",null,1.667]
[]
[]
[]
[]
["Support in verticel raceway PCM 7-32",null,null,null,"Jam Ratio PCM 7-17"]
["wire size","AL","CU",null,"0-2.4","very small"]
["18 -8","100 ft.","100 ft.",null,"2.4 -2.5","small"]
["6 - 1/0","200 ft.","100 ft.",null,"2.5-2.6","moderate"]
["2/0 - 4/0","180 ft.","80 ft.",null,"2.6 -2.9","significant"]
["250 - 350","135 ft.","60 ft.",null,"2.9-3.0","moderate"]
["400 - 500","120 ft.","50 ft.",null,"3.0-3.2","small"]
["600 - 750","95 ft.","40 ft.",null,"3.2 -up","very small"]
["900 - 1000","85 ft","35 ft."]
[]
[]
[]
[]
[]
[]
["Acceptable Megger reading"]
["Per Dave Mercier Jan 2009"]
["use ","50 - infinity "]
[]
["Formula is: (cable length X Resistance X temperature factor) Divided by 1000"]
[]
["size","type","length / ft.","temp 65","resistance"]
[350,"THHN",300,1.34,240]
[]
[]
["Min installation temp PCM 7-2",null,null,null,"Minimum Operation Temp"]
["THHN","-10C (14F)",null,null,"THHN","-25C (-10 F) THHN"]
["XLP","-40C (-40F)",null,null,"XHHW","-40 C (-40F) XHHW"]
[]
["Number of current carrying conductors BWHB 100"]
["            conductors","Correction factor"]
["            1-3",1]
["            4-6",0.8]
["            7-9",0.7]
["            10-20",0.5]
["            21-30",0.45]
["            31-40",0.4]
["            41 up",0.35]
[]
["Max allowable conductor Stress  PCM 7-10",{"$nulls":5},"Conductor Short Circuit Factors, Fc"]
["CU /soft",0.008,"per cmil",null,null,null,"Insulation","Copper","Aluminum"]
["AL / 8000 ",0.006,"per cmil",null,null,null,"Thermoset (XLPE, ERP) 105 - 250",0.0678,0.0443]
["Max",10000,{"$nulls":4},"Thermoset (XLPE, ERP)  90-250",0.0719,0.047]
["Basket grips",1000,{"$nulls":4},"Thermoplastic (PVC, PE) 75 - 100",0.0529,0.0346]
[]
[]
["Ambient Temp correction factors for CU and AL",null,null,null,"PCM 6-31"]
["Ambient Temp ",null,"60C","75C","90C"]
[]
[]
["     21-25C (70-75F)",null,1.08,1.05,1.04]
["     26-30C (78-86F)",null,1,1,1]
["     31-35C (87-95F)",null,0.91,0.94,0.96]
["     36-40C (96-104F)",null,0.82,0.88,0.91]
["     41-45C (105-113F)",null,0.71,0.82,0.87]
["     51-55C (114-122F)",null,0.58,0.75,0.82]
["     56-60C (123-131F)",null,0.41,0.67,0.76]
["     61-70C (141-158F)",null,null,0.58,0.71]
["     71-80C (159-176F)",null,null,0.33,0.58]
[{"$nulls":4},0.41]
[]
["Stranding"]
["AL","Compact AA-8000 Series Alloy Class B"]
["CU","Compressed Soft CU Class B"]
[]
[]
["Power Cable Drop Downs"]
[null,null,"Cable Conductor Count"]
[{"$nulls":4},"Voltage / Ins Level / Shield"]
["CU or AL",{"$nulls":8},"Armor",null,"Jacket"]
["CU",null,"1 / C",null,null,null,"600V RHH RHW USE (XLP) ",null,null,"No",null,"No"]
["AL",null,"3 / C WG",null,null,null,"600V XHHW ( XLP)",null,null,"Steel ",null,"PVC"]
[null,null,"4 / C WG",null,null,null,"600V THHN THWN",null,null,"Aluminum (AIA)",null,"SIMpull-PVC"]
[{"$nulls":6},"1kV Non Shielded",null,null,"Armor-X (CCA)",null,"CPE-PO"]
[{"$nulls":6},"2.4 kV Non Shielded",null,null,"Tech 90",null,"CPE-XLP"]
[{"$nulls":6},"5kV 115 Mil EPR 133% CU Tape",{"$nulls":4},"SOLONON PO"]
[{"$nulls":6},"15kV 175 Mil EPR 100% CU Tape",{"$nulls":4},"SOLONON XPL"]
[{"$nulls":6},"15kV 220 Mil EPR 133% CU Tape",{"$nulls":4},"SIMpull SOLONON XLP"]
[{"$nulls":6},"25kV 260 MIL EPR 100% CU Tape"]
[{"$nulls":6},"28kV 280 MIL EPR 100% CU Tape"]
[{"$nulls":6},"35kV 345 MIL EPR 100% CU Tape"]
[{"$nulls":6},"35kV 420 Mil EPR 133% CU Tape"]
[{"$nulls":6},"2kV XLP  RHH / RHW-2 "]
[]
[null,null,"Elbow Centerline Radius (inches)",{"$nulls":8},"EMT",null,"PVC Sch 40 & HDPE",null,"PVC Sch 80",null,"Flex FMC",null,"GRC",null,"Flex  LFMC & LFNC-B",null,"RTRC IPS Fiberglass",null,"IMC"]
["Conduit Size","Standard",12,15,18,24,30,36,42,48,null,"Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID"]
[0.375,"N/A",0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,null,"N/A",null,"N/A",null,"N/A",null,0.375,0.384,"N/A",null,0.375,0.494,"N/A",null,"N/A"]
[0.5,0.333,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,null,0.5,0.622,0.5,0.602,0.5,0.526,0.5,0.635,0.5,0.632,0.5,0.632,"N/A",null,0.5,0.66]
[0.75,0.375,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,null,0.75,0.824,0.75,0.804,0.75,0.722,0.75,0.824,0.75,0.836,0.75,0.83,0.75,0.91,0.75,0.864]
[1,0.479,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,null,1,1.049,1,1.029,1,0.936,1,1.02,1,1.063,1,1.054,1,1.175,1,1.105]
[1.25,0.604,0.94,1.19,1.44,1.94,2.44,2.94,3.44,3.94,null,1.25,1.38,1.25,1.36,1.25,1.255,1.25,1.275,1.25,1.394,1.25,1.395,1.25,1.52,1.25,1.448]
[1.5,0.687,0.93,1.18,1.43,1.93,2.43,2.93,3.43,3.93,null,1.5,1.61,1.5,1.59,1.5,1.476,1.5,1.538,1.5,1.624,1.5,1.588,1.5,1.76,1.5,1.683]
[2,0.792,0.91,1.16,1.41,1.91,2.41,2.91,3.41,3.91,null,2,2.067,2,2.047,2,1.913,2,2.04,2,2.083,2,2.033,2,2.235,2,2.15]
[2.5,0.875,null,1.15,1.4,1.9,2.4,2.9,3.4,3.9,null,2.5,2.731,2.5,2.445,2.5,2.29,2.5,2.5,2.5,2.489,2.5,2.493,2.5,2.74,2.5,2.557]
[3,1.08,null,null,1.37,1.87,2.37,2.87,3.37,3.87,null,3,3.356,3,3.042,3,2.864,3,3,3,3.09,3,3.085,3,3.36,3,3.176]
[3.5,1.25,null,null,1.35,1.85,2.35,2.85,3.35,3.85,null,3.5,3.834,3.5,3.521,3.5,3.326,3.5,3.5,3.5,3.57,3.5,3.52,"N/A",null,3.5,3.671]
[4,1.33,null,null,null,1.83,2.33,2.83,3.33,3.83,null,4,4.334,4,3.998,4,3.786,4,4,4,4.05,4,4.02,4,4.32,4,4.166]
[5,2,{"$nulls":4},2.29,2.79,3.29,3.79,null,null,null,5,5.016,5,4.768,null,null,5,5.073,null,null,5,5.38]
[6,2.5,{"$nulls":5},2.75,3.25,3.75,null,null,null,6,6.031,6,5.709,null,null,6,6.093,null,null,6,6.435]
[]
[]
["Coefficient of Friction (COF) in Duct"]
[null,null,"Steel or Aluminum","PVC","Fiber (Orangeburg) (Nocrete)","ASB          Asbestos Cement (Transite, Korduct)","Cable Tray"]
[]
[null,"Notes"]
["Jacket type"]
["PVC",null,0.4,0.35,0.5,0.5,0.15]
["SIMpull PVC","Exclusive to Southwire",0.2,0.2]
["PE",null,0.35,0.35,0.5,0.5,0.15]
["CSPE (Hypalon)","No longer made",0.5,0.5,0.7,0.6]
["CPE (PO)",null,0.5,0.5,0.7,0.6,0.15]
["CPE (XLP)"]
["SOLONON (LSZH-PO)","Exclusive to Southwire",0.35,0.35,0.5,0.5,0.15]
["SOLONON (LSZH-XLP)","Exclusive to Southwire",{"$nulls":4},0.15]
["SIMpull SOLONON ","Exclusive to Southwire",{"$nulls":4},0.15]
["Source PCM 7-14",{"$nulls":5},"Per Paul White 12-8-09"]
[]
[]
[]
["Jacket Definations:"]
["PVC","Polyvinal Choloride (thermoplastic)"]
["SIMpull","No lube required for installation in conduit.  Reduced COF."]
["CPE","Chlorinated Polyethylene"]
["CSPE (no longer made)","Chlorosulfinated???? Polyethylene (thermoset) DuPont tradename is Hypalon"]
["PO","Polyolefin???? (thermoplastic)"]
["XLP","Cross linked Polyethylene (thermoset)"]
["SOLONON","SOuthwire LOw smoke NON-halogen"]
["LSZH","Low Smoke Zero Halogen"]

{"sheet":"Maxis Grips","index":16,"n_rows":40,"n_cols":13,"rows_kept":40,"cut":false,"hidden":true,"merged":[[23,12,23,13],[24,12,24,13],[23,4,23,5],[39,4,39,5],[40,4,40,5],[34,4,34,5],[35,4,35,5],[36,4,36,5],[37,4,37,5],[38,4,38,5],[27,0,28,0],[27,1,28,1],[27,2,28,2],[27,3,28,3],[32,4,32,5],[33,4,33,5],[27,8,27,10],[24,4,24,5],[29,4,29,5],[30,4,30,5],[27,4,28,5],[22,4,22,5],[19,4,19,5],[19,12,19,13],[21,4,21,5],[20,12,20,13],[21,12,21,13],[22,12,22,13],[20,4,20,5],[1,0,1,14],[11,0,12,0],[11,1,12,1],[11,2,12,2],[11,3,12,3],[11,9,12,9],[11,12,12,13],[11,4,12,5],[11,10,12,10],[15,4,15,5],[11,8,12,8],[17,12,17,13],[18,12,18,13],[11,11,12,11],[13,12,13,13],[14,12,14,13],[13,4,13,5],[14,4,14,5],[15,12,15,13],[16,4,16,5],[16,12,16,13],[17,4,17,5],[18,4,18,5]],"flags":["formulas_cached_only"]}
[]
["Important installation Instruction for Maxis Grips and Jacket"]
[]
["Just because the grips fit the wire does not mean the grips will fit into your conduit size.  "]
[]
["Use no more than four Maxis double locking grips on a pull, serve your GW or use the basket grip."]
[]
["When using the jacket you will probably need to remove the conduit insert part "]
["of the adapter before the jacket reaches the end of the pull."]
[]
[]
["SIMpull CU THHN","Maxis Size Grip","SIMpull AL THHN","Maxis Size Grip","Min size conduit using 4 grips & jacket",null,null,null,"SIMpull CU XHHW","Maxis Size Grip","AL XHHW","Maxis Size Grip","Min size conduit using 4 grips & jacket"]
[]
["1/0","AA","2/0","AA",{"$nulls":4},"1/0","AA","2/0","AA"]
["2/0","AA","3/0","AA",{"$nulls":4},"2/0","AA","3/0","AA"]
["3/0","A","4/0","A",2,null,null,null,"3/0","A","4/0","A",2]
["4/0","A",250,"A",2.5,null,null,null,"4/0","A",250,"A",2.5]
[250,"B","300","B",3,null,null,null,250,"B","300","B",3]
["300","B","350","B",3,null,null,null,"300","B","350","B",3]
["350","B","400","B",3,null,null,null,"350","B","400","B",3]
["400","C","500","C",3,null,null,null,"400","C","500","C",3]
["500","C","600","C",3.5,null,null,null,"500","C","600","C",3.5]
["600","D","750","D",4,null,null,null,"600","D","750","D",4]
["750","D","900","D",4,null,null,null,"750","D","900","D",4]
[]
[]
[]
["CU USE","Maxis Size Grip","AL USE","Maxis Size Grip","Min size conduit using 4 grips & jacket",null,null,null,"Maxis Grip OD Range Per David "]
[{"$nulls":8},"Size","Min Dia","Max Dia"]
["1/0","AA","2/0","AA",{"$nulls":4},"AA",0.474,0.624]
["2/0","AA","3/0","A",{"$nulls":4},"A",0.568,0.673]
["3/0","A","4/0","A",null,null,2,null,"B",0.678,0.809]
["4/0","A",250,"B",2,null,2.5,null,"C",0.821,0.976]
[250,"B","300","B",2.5,null,3,null,"D",0.983,1.191]
["300","B","350","B",3,null,3,null,"Confirmed by Rudy 12-20-12"]
["350","B","400","C",3,null,3]
["400","C","500","C",3,null,3]
["500","D","750","D",3.5,null,4]
["600","D",null,null,3.5,null,4]
["750","D",null,null,4]

{"sheet":"Tension Calc","index":17,"n_rows":88,"n_cols":45,"rows_kept":88,"cut":false,"hidden":true,"merged":[[76,7,79,14]],"flags":["formulas_cached_only"]}
["Bend Section Angle in Radians",{"$nulls":4},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,null,null,null,"CU THHn","S-1","1-2","2-3","3-4","4-5","5-6","6-7","7-8","8-9","9-10","10-11","11-12","12-13","13-14","14-15","15-16","16-17","17-18"]
["Degrees","Radian",null,"Tension In","Tin","25",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,"Tin","25",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[90,1.5707963267948966,null,"Tension out","Tout",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,"Tout",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[75,1.3089969389957472,null,"Length","L",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,"L",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[60,1.0471975511965976,null,"Straight Section Radians","q",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,"q",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[55,0.9599310885968813,null,"Bend Section Radians","f",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"},null,null,null,"f",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
[50,0.8726646259971648,null,"Side Pressure","SP",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,"SP",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[45,0.7853981633974483,null,"Bend Radius (ft)","R",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"},null,null,null,"R",0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5,{"$error":"#VALUE!"}]
[35,0.6108652381980153,null,"Allow Stress (lbs/cmil)","S",0.008,{"$nulls":20},"S",0.008]
[30,0.5235987755982988,null,"Area of Conductor (cmil)","A",0,"Seg",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,null,"A",0]
[25,0.4363323129985824,null,"Number of Conductors","N",0,"in",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"N",0]
[22.5,0.39269908169872414,null,"Wt Corr. Fct. ","w",1.4,"out",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"w",1.4]
[15,0.2617993877991494,null,"Coefficient of Friction","m",0,1,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"m",0.35]
[11.25,0.19634954084936207,null,"Total Cable Wt. (Lbs/ft)","W",0,2,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"W",0]
[10,0.17453292519943295,null,"Natural Logarithm base","e",2.718281828459045,3,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"e",2.718281828459045]
[0,0,null,"Tension On Each Conductor (lbs)","TC",0,4,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"TC",0]
[0,0,null,"Max allowable tension on device (lbs)","Tcable",0,5,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"Tcable",0]
[0,0,null,"Conduit Inner Diameter ","D",0.622,6,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"D",0.622]
[0,0,null,"Outter Diameter of Cable","d",0,7,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,"d",0]
[null,null,null,"Conductor short circuit factor","Fc",0.0529,8,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":4},"t",0.0667]
[{"$nulls":4},"wm2",0]
[{"$nulls":4},"ewmf",1]
[null,null,null,"Typical COF",null,0.35,null,null,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false]
[{"$nulls":4},"Area of Conductor (cmil) for Short circuit calc",0]
[]
[{"$nulls":4},3.3,"Very Small"]
[]
[null,"Conductor Stress",null,null,"Jam Table",null,null,"In2",{"$nulls":4},"Maximum SP",null,null,"CU THHN"]
[null,"Type","lb/cmil",null,0,"Very Small",null,"Cable 1","Cable 2","Cable 3","Total",null,"SIMpull THHN",1000,null,"Cable","Size","OD","Wt","Amps","Count"]
[null,"CU",0.008,null,2.4,"Small",null,0,0,0,0,null,"XHHW",500,1,1,0,0,0,0,0]
[null,"AL",0.006,null,2.5,"Moderate",{"$nulls":7},"wire size",1,2,0,0,0,0,0]
[{"$nulls":4},2.6,"Significant",{"$nulls":7},1,1,3,0,0,0,0,0]
[{"$nulls":4},2.9,"Moderate",{"$nulls":7},1,null,"Totals",null,0,0,null,0]
[null,"Tension Info",null,null,3,"Small",{"$nulls":7},1]
[1,0,4,null,3.2,"Very Small",{"$nulls":7},"al",null,"AL THHN"]
[2,0,4,{"$nulls":7},"Used in tension and sidewall calc ",{"$nulls":4},"Cable","Size","OD","Wt","Amps","Count"]
[3,0,4,{"$nulls":4},"Minimum Bend",null,null,1,null,null,null,1,1,0,0,0,0,0]
[4,0,4,{"$nulls":4},0,4,{"$nulls":5},1,2,0,0,0,0,0]
[5,0,4,{"$nulls":4},1,5,{"$nulls":5},1,3,0,0,0,0,0]
[6,0,4,{"$nulls":4},2.1,6,{"$nulls":6},"Totals",null,0,0,null,0]
[7,0,4]
[8,0,4]
[9,0,4,{"$nulls":4},"Typical COF",0.35]
[10,0,4,{"$nulls":4},"Not Recommended Tension and Side wall pressure"]
[11,0,4,null,null,null,"Seg",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[12,0,4,null,null,null,"in",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[13,0,4,null,null,null,"out",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[14,0,4,null,null,null,1,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[15,0,4,null,null,null,2,25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[16,0,4,null,null,null,3,25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[17,0,4,null,null,null,4,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[18,0,4,null,null,null,5,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":6},6,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":6},7,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":6},8,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":6},"SP",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[]
[{"$nulls":7},"Graph for max tension that will yield max SWP of 1000 lb",{"$nulls":4},"Graph for max tension that will yield max SWP of 500 lb"]
[{"$nulls":7},"Conduit","x","y","z",null,"Conduit","x","y","z"]
[{"$nulls":7},"size","std elbow","36\" elbow","48\" elbow",null,"size","std elbow","36\" elbow","48\" elbow"]
[{"$nulls":7},0.5,475,"Calc","Calc",null,0.5,238,"Calc","Calc"]
[{"$nulls":7},0.75,535,"Calc","Calc",null,0.75,268,"Calc","Calc"]
[{"$nulls":6},0.5,1,685,"Calc","Calc",null,1,342,"Calc","Calc"]
[{"$nulls":7},1.25,860,"Calc","Calc",null,1.25,431,"Calc","Calc"]
[{"$nulls":7},1.5,980,"Calc","Calc",null,1.5,490,"Calc","Calc"]
[{"$nulls":7},2,1130,4155,"Calc",null,2,565,2077,"Calc"]
[1,5,{"$nulls":5},2.5,1250,4146,5570,null,2.5,624,2070,2783]
[1,5,{"$nulls":5},3,1540,4090,5535,null,3,771,2048,2762]
[1,5,{"$nulls":5},3.5,1785,4070,5499,null,3.5,892,2034,2747]
[1,5,{"$nulls":5},4,1900,4040,5465,null,4,949,2020,2733]
[1,5,{"$nulls":5},5,2850,3983,5410,null,5,1428,1991,2705]
[1,5,{"$nulls":5},6,3571,3923,5350,null,6,1784,1963,2671]
[1,5,{"$nulls":5},"On line 13, 14 & 15 of the sketch sheet:"]
[1,5,{"$nulls":5},"This pull will reach a maximium sidewall pressure of 1000 lbs when tensions reach (x )lbs when using a std radius elbow, (y) lbs when using a 36\" radius elbow, (z) lbs when using a 48\" radius elbow."]
[1,5]
[1,5]
[1,5]
[1,5]
[1,5,{"$nulls":5},"SWP of 1000 lb occurs at approx 475 lbs of pulling force using std. radius elbows."]
[1,5,{"$nulls":5},"SWP of 1000 lb occurs at approx Calc lbs of pulling force using 36 in.radius elbows."]
[1,5,{"$nulls":5},"SWP of 1000 lb occurs at approx Calc lbs of pulling force using 48 in.radius elbows."]
[1,5]
[1,5,{"$nulls":5},"SWP of 500 lb occurs at approx 238 lbs of pulling force using std. radius elbows."]
[1,5,{"$nulls":5},"SWP of 500 lb occurs at approx Calc lbs of pulling force using 36 in.radius elbows."]
[{"$nulls":7},"SWP of 500 lb occurs at approx Calc lbs of pulling force using 48 in.radius elbows."]

{"sheet":"Power Cable Tension Calc ","index":18,"n_rows":94,"n_cols":32,"rows_kept":94,"cut":false,"hidden":true,"merged":[[31,4,31,5],[76,7,79,14]],"flags":["formulas_cached_only"]}
["Bend Section Angle in Radians",{"$nulls":4},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
["Degrees","Radian",null,"Tension In","Tin","25",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[90,1.5707963267948966,null,"Tension out","Tout",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[75,1.3089969389957472,null,"Length","L",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[60,1.0471975511965976,null,"Straight Section Radians","q",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[55,0.9599310885968813,null,"Bend Section Radians","f",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
[50,0.8726646259971648,null,"Side Pressure","SP",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[45,0.7853981633974483,null,"Bend Radius (ft)","R",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
[45,0.7853981633974483,null,"Allow Stress (lbs/cmil)","S",0.008]
[30,0.5235987755982988,null,"Area of Conductor (cmil)","A",0,"Seg",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[25,0.4363323129985824,null,"Number of Cables","N",0,"in",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[22.5,0.39269908169872414,null,"Wt Corr. Fct. ","w",1.4,"out",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[15,0.2617993877991494,null,"Coefficient of Friction","m",0.2,1,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[11.25,0.19634954084936207,null,"Total Cable Wt. (Lbs/ft)","W",0,2,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[10,0.17453292519943295,null,"Natural Logarithm base","e",2.718281828459045,3,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[0,0,null,"Tension On Each Conductor (lbs)","TC",0,4,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[0,0,null,"Max allowable tension on device (lbs)","Tcable",0,5,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[0,0,null,"Conduit Inner Diameter ","D",0.622,6,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[0,0,null,"Outter Diameter of Cable","d",1.505,7,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,null,null,"Conductor short circuit factor","Fc",0.0678,8,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":4},"t",0.0333]
[{"$nulls":4},"wm2",0.07839999999999998]
[{"$nulls":4},"ewmf",1]
[null,null,null,"Typical COF",null,0.35,null,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false,false]
[{"$nulls":4},"Area of Conductor (cmil) for Short circuit calc",500000]
[null,"Short Cir Factor",null,null,"D/d",0.41328903654485055]
[null,0.0678,null,null,3.3,"Very Small"]
[{"$nulls":4},"FC",0.0678]
[null,"Conductor Stress",null,null,"ISC",185770.85565505372,null,"In2",{"$nulls":4},"Maximum SP",null,null,"CU THHN"]
[null,"Type","lb/cmil",null,"Metal Area used for tensions",0,null,"Cable 1","Cable 2",null,"Total",null,"SIMpull THHN",1000,null,"Cable","Size","OD","Wt","Amps","Count"]
[null,"CU",0.008,{"$nulls":4},0,0,0,0,null,"XHHW",500,null,1,"500",0.752,0.418,250,0]
[null,"AL",0.006,null,"Jam Probablity",{"$nulls":10},2,0,0,0,0,0]
[{"$nulls":4},0.41328903654485055,"Very Small",{"$nulls":7},"Type","Size","Totals",null,0,0,null,0]
[{"$nulls":4},"Jam Table",{"$nulls":4},"16","Was in cell D12 of Calc for PC",null,null,1,"16"]
[null,"Tension Info",null,null,0,"Very Small",{"$nulls":7},1,1]
[1,0,4,null,2.4,"Small",{"$nulls":9},"AL THHN"]
[2,0,4,null,2.5,"Moderate",{"$nulls":4},"Used in tension and sidewall calc ",{"$nulls":4},"Cable","Size","OD","Wt","Amps","Count"]
[3,0,4,null,2.6,"Significant",null,"Minimum Bend",null,null,1,{"$nulls":4},1,0,0,0,0,0]
[4,0,4,null,2.9,"Moderate",null,0,4,{"$nulls":6},2,0,0,0,0,0]
[5,0,4,null,3,"Small",null,1,5,{"$nulls":6},"Totals",null,{"$error":"#VALUE!"},{"$error":"#VALUE!"},null,0]
[6,0,4,null,3.2,"Very Small",null,2.1,6]
[7,0,4]
[8,0,4]
[9,0,4,{"$nulls":4},"Typical COF",{"$error":"#VALUE!"}]
[10,0,4,{"$nulls":4},"Not Recommended Tension and Side wall pressure"]
[11,0,4,null,null,null,"Seg",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[12,0,4,null,null,null,"in",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[13,0,4,null,null,null,"out",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[14,0,4,null,null,null,1,25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[15,0,4,null,null,null,2,25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[16,0,4,null,null,null,3,25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[17,0,4,null,null,null,4,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[18,0,4,null,null,null,5,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[19,0,4,null,null,null,6,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[20,0,4,null,null,null,7,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[21,0,4,null,null,null,8,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[22,0,4]
[23,0,4,null,null,null,"SP",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[24,0,4]
[25,0,4]
[{"$nulls":7},"Graph for max tension that will yield max SWP of 1000 lb",{"$nulls":4},"Graph for max tension that will yield max SWP of 500 lb"]
[{"$nulls":7},"Conduit","x","y","z",null,"Conduit","x","y","z"]
[{"$nulls":7},"size","std elbow","36\" elbow","48\" elbow",null,"size","std elbow","36\" elbow","48\" elbow"]
[{"$nulls":7},0.5,476,4227,5655,null,0.5,238,2112,2826]
[{"$nulls":7},0.75,536,4227,5655,null,0.75,268,2112,2826]
[{"$nulls":7},1,986,4227,5655,null,1,492,2112,2826]
[{"$nulls":6},0.5,1.25,863,4198,5626,null,1.25,431,2098,2812]
[{"$nulls":7},1.5,981,4184,5612,null,1.5,490,2091,2805]
[{"$nulls":7},2,1131,4155,5583,null,2,565,2077,2790]
[1,4,{"$nulls":5},2.5,1249,4141,5569,null,2.5,625,2070,2783]
[1,4,{"$nulls":5},3,1543,4098,5526,null,3,771,2048,2762]
[1,4,{"$nulls":5},3.5,1785,4070,5498,null,3.5,892,2034,2748]
[1,4,{"$nulls":5},4,1899,4041,5469,null,4,950,2020,2734]
[1,4,{"$nulls":5},5,"Calc","Calc","Calc",null,5,"Calc","Calc","Calc"]
[1,4,{"$nulls":5},6,"Calc","Calc","Calc",null,6,"Calc","Calc","Calc"]
[1,4,{"$nulls":5},"On line 13, 14 & 15 of the sketch sheet:"]
[1,4,{"$nulls":5},"This pull will reach a maximium sidewall pressure of 1000 lbs when tensions reach (x )lbs when using a std radius elbow, (y) lbs when using a 36\" radius elbow, (z) lbs when using a 48\" radius elbow."]
[1,4]
[1,4]
[1,4]
[1,4]
[1,4,{"$nulls":5},"SWP of 1000 lb occurs at approx 476 lbs of pulling force using std. radius elbows."]
[1,4,{"$nulls":5},"SWP of 1000 lb occurs at approx 4227 lbs of pulling force using 36 in.radius elbows."]
[1,4,{"$nulls":5},"SWP of 1000 lb occurs at approx 5655 lbs of pulling force using 48 in.radius elbows."]
[1,4]
[1,4,{"$nulls":5},"SWP of 500 lb occurs at approx 238 lbs of pulling force using std. radius elbows."]
[1,4,{"$nulls":5},"SWP of 500 lb occurs at approx 2112 lbs of pulling force using 36 in.radius elbows."]
[1,4,{"$nulls":5},"SWP of 500 lb occurs at approx 2826 lbs of pulling force using 48 in.radius elbows."]
[1,4]
[1,4]
[1,4]
[1,4]
[1,4]
[1,4]

{"sheet":"Conduit","index":19,"n_rows":73,"n_cols":59,"rows_kept":73,"cut":false,"hidden":true,"merged":[[0,19,0,20],[40,19,40,20]],"flags":["formulas_cached_only"]}
[null,null,null,"EMT",null,"PVC Sch 40 & HDPE",null,"PVC Sch 80",null,"Flex FMC",null,"GRC",null,"Flex  LFMC & LFNC-B",null,"RTRC IPS Fiberglass",null,"IMC",null,"Cable Tray",{"$nulls":4},"Elbow Centerline Radius (inches)",{"$nulls":18},"Elbow Centerline Radius (inches)"]
["1","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID",null,"Conduit Size","Standard",12,15,18,24,30,36,42,48,"3\" RR","6\"RR","9\" RR","12\" RR","UBR # 1","UBR # 2","UBR # 3","UBR # 4",null,"Conduit Size","Standard",12,15,18,24,30,36,42,48,"3\" RR","6\"RR","9\" RR","12\" RR","UBR # 1","UBR # 2","UBR # 3","UBR # 4"]
[null,"N/A",0,"N/A",null,"N/A",null,"N/A",null,0.375,0.384,"N/A",null,0.375,0.494,"N/A",null,"N/A",null,"Any Size","N/A",null,0.375,"N/A",0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0,null,0.375,"N/A",0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0]
[null,0.5,0.622,0.5,0.622,0.5,0.602,0.5,0.526,0.5,0.635,0.5,0.632,0.5,0.632,"N/A",null,0.5,0.66,"Any Size","N/A",null,0.5,0.333,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0,null,0.5,0.333,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0]
[null,0.75,0.824,0.75,0.824,0.75,0.804,0.75,0.722,0.75,0.824,0.75,0.836,0.75,0.83,0.75,0.91,0.75,0.864,"Any Size","N/A",null,0.75,0.375,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0,null,0.75,0.375,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0]
[null,1,1.049,1,1.049,1,1.029,1,0.936,1,1.02,1,1.063,1,1.054,1,1.175,1,1.105,"Any Size","N/A",null,1,0.479,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0,null,1,0.69,0.96,1.21,1.46,1.96,2.46,2.96,3.476,3.96,{"$nulls":4},0,0,0,0]
[null,1.25,1.38,1.25,1.38,1.25,1.36,1.25,1.255,1.25,1.275,1.25,1.394,1.25,1.395,1.25,1.52,1.25,1.448,"Any Size","N/A",null,1.25,0.604,0.94,1.19,1.44,1.94,2.44,2.94,3.44,3.94,{"$nulls":4},0,0,0,0,null,1.25,0.604,0.94,1.19,1.44,1.94,2.44,2.94,3.44,3.94,{"$nulls":4},0,0,0,0]
[null,1.5,1.61,1.5,1.61,1.5,1.59,1.5,1.476,1.5,1.538,1.5,1.624,1.5,1.588,1.5,1.76,1.5,1.683,"Any Size","N/A",null,1.5,0.687,0.93,1.18,1.43,1.93,2.43,2.93,3.43,3.93,{"$nulls":4},0,0,0,0,null,1.5,0.687,0.93,1.18,1.43,1.93,2.43,2.93,3.43,3.93,{"$nulls":4},0,0,0,0]
[null,2,2.067,2,2.067,2,2.047,2,1.913,2,2.04,2,2.083,2,2.033,2,2.235,2,2.15,"Any Size","N/A",null,2,0.792,0.91,1.16,1.41,1.91,2.41,2.91,3.41,3.91,{"$nulls":4},0,0,0,0,null,2,0.792,0.91,1.16,1.41,1.91,2.41,2.91,3.41,3.91,{"$nulls":4},0,0,0,0]
[null,2.5,2.731,2.5,2.731,2.5,2.445,2.5,2.29,2.5,2.5,2.5,2.489,2.5,2.493,2.5,2.74,2.5,2.557,"Any Size","N/A",null,2.5,0.875,null,1.15,1.4,1.9,2.4,2.9,3.4,3.9,0.25,0.5,0.75,1,0,0,0,0,null,2.5,0.875,null,1.15,1.4,1.9,2.4,2.9,3.4,3.9,0.25,0.5,0.75,1,0,0,0,0]
[null,3,3.356,3,3.356,3,3.042,3,2.864,3,3,3,3.09,3,3.085,3,3.36,3,3.176,"Any Size","N/A",null,3,1.08,null,null,1.37,1.87,2.37,2.87,3.37,3.87,0.25,0.5,0.75,1,0,0,0,0,null,3,1.08,null,null,1.37,1.87,2.37,2.87,3.37,3.87,0.25,0.5,0.75,1,0,0,0,0]
[null,3.5,3.834,3.5,3.834,3.5,3.521,3.5,3.326,3.5,3.5,3.5,3.57,3.5,3.52,"N/A",null,3.5,3.671,"Any Size","N/A",null,3.5,1.25,null,null,1.35,1.85,2.35,2.85,3.35,3.85,0.25,0.5,0.75,1,0,0,0,0,null,3.5,1.25,null,null,1.35,1.85,2.35,2.85,3.35,3.85,0.25,0.5,0.75,1,0,0,0,0]
[null,4,4.334,4,4.334,4,3.998,4,3.786,4,4,4,4.05,4,4.02,4,4.32,4,4.166,"Any Size","N/A",null,4,1.33,null,null,null,1.83,2.33,2.83,3.33,3.83,0.25,0.5,0.75,1,0,0,0,0,null,4,1.33,null,null,null,1.83,2.33,2.83,3.33,3.83,0.25,0.5,0.75,1,0,0,0,0]
[null,0,0,null,null,5,5.016,5,4.768,null,null,5,5.073,null,null,5,5.38,null,null,"Any Size","N/A",null,5,2,{"$nulls":4},2.29,2.79,3.29,3.79,0.25,0.5,0.75,1,0,0,0,0,null,5,2,{"$nulls":4},2.29,2.79,3.29,3.79,0.25,0.5,0.75,1,0,0,0,0]
[null,0,0,null,null,6,6.031,6,5.709,null,null,6,6.093,null,null,6,6.435,null,null,"Any Size","N/A",null,6,2.5,{"$nulls":5},2.75,3.25,3.75,0.25,0.5,0.75,1,0,0,0,0,null,6,2.5,{"$nulls":5},2.75,3.25,3.75,0.25,0.5,0.75,1,0,0,0,0]
[null,0,0,{"$nulls":16},"Any Size","N/A",null,"Any Size",null,1,1.25,1.5,2,2.5,3,3.5,4,0.25,0.5,0.75,1,0,0,0,0,null,"Any Size",null,1,1.25,1.5,2,2.5,3,3.5,4,0.25,0.5,0.75,1,0,0,0,0]
[null,null,null,0,null,"600V %","Pwr Cab %"]
[{"$nulls":5},0.40799,0.40799]
[null,null,"Table8",{"$nulls":9},"Lookup Table",{"$nulls":7},0.5,2,2]
[null,"Size","EMT","PVC 40","PVC 80","Flex FMC","GRC","Flex LFMC","RTRC","IMC",null,"Value","EMT","PVC","PVC","Flex FMC","GRC","Flex LFMC","RTRC","IMC","Size"]
[null,0.375,"N/A","N/A","N/A",0.04632466863277365,"N/A",0.07666617048114388,"N/A","N/A",null,"N/A","N/A",11.655155088256953,10.443822591102379,"N/A",11.896021929369551,"N/A",13.268948311893745,"N/A",6,13]
[null,0.5,0.12397101850369575,0.11612677957685856,0.08865656247228763,0.12920724024811756,0.12798926834611968,0.12798926834611968,"N/A",0.13958131031577908,null,"N/A","N/A",8.062216483839398,7.284703724536972,"N/A",8.24648976865856,"N/A",9.274787140275564,"N/A",5,12]
[null,0.75,0.21756740071847194,0.20713405025042392,0.1670374282980959,0.21756740071847194,0.22395045788442772,0.2207473936559692,0.26535188951445515,0.2392031446866111,null,6.018901191161188,6.018901191161188,5.121827875143834,4.5930441402182565,5.126953546952399,5.25592847211792,5.178351256260595,5.980078617165279,5.561320587095688,4,11]
[null,1,0.3526065506262479,0.33928928878803905,0.2807314684169256,0.3333801543905798,0.3620811607810159,0.3559759204103857,0.4424000150475723,0.39125865341672206,null,4.710246298301589,4.710246298301589,3.972569006755193,3.5447359484728995,3.9253238093854304,4.0839068912846015,3.9703128267599377,"N/A",4.318253849658459,3.5,10]
[null,1.25,0.6102356459260091,0.5926758300276975,0.5046925006430438,0.5209064912352808,0.6226800439228495,0.6235737360130027,0.7403320921799265,0.6718565006068302,null,3.6089702677242794,3.6089702677242794,2.9652261351537756,2.628363497566429,2.8839113701607246,3.0595415726035124,3.0496481544308778,3.6175784227296126,3.2322160863264835,3,9]
[null,1.5,0.8305985180659571,0.8100907038781475,0.6980911219065856,0.7579700941198294,0.8451065148654457,0.8080540215816209,0.9925782066899844,0.9076274703283533,null,2.38991689896259,2.38991689896259,1.9155660298450068,1.6803910684733172,2.0027162292782807,1.9851310990468305,1.9915167196895598,2.4056947780687397,2.0950811813379984,2.5,8]
[null,2,1.3690532895540695,1.3426879309388666,1.1726525165541903,1.333520617562319,1.390330146773922,1.3243847067762464,1.600642908223456,1.4812089231742163,null,1.3690532895540695,1.3690532895540695,1.3426879309388666,1.1726525165541903,1.333520617562319,1.390330146773922,1.3243847067762464,1.600642908223456,1.4812089231742163,2,7]
[null,2.5,2.38991689896259,1.9155660298450068,1.6803910684733172,2.0027162292782807,1.9851310990468305,1.9915167196895598,2.4056947780687397,2.0950811813379984,null,0.8305985180659571,0.8305985180659571,0.8100907038781475,0.6980911219065856,0.7579700941198294,0.8451065148654457,0.8080540215816209,0.9925782066899844,0.9076274703283533,1.5,6]
[null,3,3.6089702677242794,2.9652261351537756,2.628363497566429,2.8839113701607246,3.0595415726035124,3.0496481544308778,3.6175784227296126,3.2322160863264835,null,0.6102356459260091,0.6102356459260091,0.5926758300276975,0.5046925006430438,0.5209064912352808,0.6226800439228495,0.6235737360130027,0.7403320921799265,0.6718565006068302,1.25,5]
[null,3.5,4.710246298301589,3.972569006755193,3.5447359484728995,3.9253238093854304,4.0839068912846015,3.9703128267599377,"N/A",4.318253849658459,null,0.3526065506262479,0.3526065506262479,0.33928928878803905,0.2807314684169256,0.3333801543905798,0.3620811607810159,0.3559759204103857,0.4424000150475723,0.39125865341672206,1,4]
[null,4,6.018901191161188,5.121827875143834,4.5930441402182565,5.126953546952399,5.25592847211792,5.178351256260595,5.980078617165279,5.561320587095688,null,0.21756740071847194,0.21756740071847194,0.20713405025042392,0.1670374282980959,0.21756740071847194,0.22395045788442772,0.2207473936559692,0.26535188951445515,0.2392031446866111,0.75,3]
[null,5,0,8.062216483839398,7.284703724536972,"N/A",8.24648976865856,"N/A",9.274787140275564,"N/A",null,0.12397101850369575,0.12397101850369575,0.11612677957685856,0.08865656247228763,0.12920724024811756,0.12798926834611968,0.12798926834611968,"N/A",0.13958131031577908,0.5,2]
[null,6,0,11.655155088256953,10.443822591102379,"N/A",11.896021929369551,"N/A",13.268948311893745,"N/A",null,"N/A","N/A","N/A","N/A",0.04632466863277365,"N/A",0.07666617048114388,"N/A","N/A",0.375,1]
[]
[]
[]
[]
[]
[{"$nulls":6},"Power Cable Tables"]
[]
[null,null,null,"EMT",null,"PVC Sch 40 & HDPE",null,"PVC Sch 80",null,"Flex FMC",null,"GRC",null,"Flex  LFMC & LFNC-B",null,"RTRC IPS Fiberglass",null,"IMC",null,"Cable Tray"]
["1","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID","Size","ID"]
[null,"N/A",0,"N/A",null,"N/A",null,"N/A",null,0.375,0.384,"N/A",null,0.375,0.494,"N/A",null,"N/A",null,"Any Size","N/A"]
[null,0.5,0.622,0.5,0.622,0.5,0.602,0.5,0.526,0.5,0.635,0.5,0.632,0.5,0.632,"N/A",null,0.5,0.66,"Any Size","N/A"]
[null,0.75,0.824,0.75,0.824,0.75,0.804,0.75,0.722,0.75,0.824,0.75,0.836,0.75,0.83,0.75,0.91,0.75,0.864,"Any Size","N/A"]
[null,1,1.049,1,1.049,1,1.029,1,0.936,1,1.02,1,1.063,1,1.054,1,1.175,1,1.105,"Any Size","N/A"]
[null,1.25,1.38,1.25,1.38,1.25,1.36,1.25,1.255,1.25,1.275,1.25,1.394,1.25,1.395,1.25,1.52,1.25,1.448,"Any Size","N/A"]
[null,1.5,1.61,1.5,1.61,1.5,1.59,1.5,1.476,1.5,1.538,1.5,1.624,1.5,1.588,1.5,1.76,1.5,1.683,"Any Size","N/A"]
[null,2,2.067,2,2.067,2,2.047,2,1.913,2,2.04,2,2.083,2,2.033,2,2.235,2,2.15,"Any Size","N/A"]
[null,2.5,2.731,2.5,2.731,2.5,2.445,2.5,2.29,2.5,2.5,2.5,2.489,2.5,2.493,2.5,2.74,2.5,2.557,"Any Size","N/A"]
[null,3,3.356,3,3.356,3,3.042,3,2.864,3,3,3,3.09,3,3.085,3,3.36,3,3.176,"Any Size","N/A"]
[null,3.5,3.834,3.5,3.834,3.5,3.521,3.5,3.326,3.5,3.5,3.5,3.57,3.5,3.52,"N/A",null,3.5,3.671,"Any Size","N/A"]
[null,4,4.334,4,4.334,4,3.998,4,3.786,4,4,4,4.05,4,4.02,4,4.32,4,4.166,"Any Size","N/A"]
[null,0,0,null,null,5,5.016,5,4.768,null,null,5,5.073,null,null,5,5.38,null,null,"Any Size","N/A"]
[null,0,0,null,null,6,6.031,6,5.709,null,null,6,6.093,null,null,6,6.435,null,null,"Any Size","N/A"]
[null,0,0,{"$nulls":16},"Any Size","N/A"]
[null,null,null,0]
[]
[null,null,"Table8",{"$nulls":9},"Lookup Table",{"$nulls":7},0.5,2,2]
[null,"Size","EMT","PVC 40","PVC 80","Flex FMC","GRC","Flex LFMC & LFNC-B","RTRC","IMC",null,"Value","EMT","PVC","PVC","Flex FMC","GRC","Flex LFMC & LFNC-B","RTRC","IMC","Size"]
[null,0.375,"N/A","N/A","N/A",0.04632466863277365,"N/A",0.07666617048114388,"N/A","N/A",null,"N/A","N/A",11.655155088256953,10.443822591102379,2.8839113701607246,11.896021929369551,"N/A",13.268948311893745,"N/A",6,13]
[null,0.5,0.12397101850369575,0.11612677957685856,0.08865656247228763,0.12920724024811756,0.12798926834611968,0.12798926834611968,"N/A",0,null,"N/A","N/A",8.062216483839398,7.284703724536972,3.9253238093854304,8.24648976865856,"N/A",9.274787140275564,"N/A",5,12]
[null,0.75,0.21756740071847194,0.20713405025042392,0.1670374282980959,0.21756740071847194,0.22395045788442772,0.2207473936559692,0.26535188951445515,0.13958131031577908,null,6.018901191161188,6.018901191161188,5.121827875143834,4.5930441402182565,5.126953546952399,5.25592847211792,5.178351256260595,5.980078617165279,4.318253849658459,4,11]
[null,1,0.3526065506262479,0.33928928878803905,0.2807314684169256,0.3333801543905798,0.3620811607810159,0.3559759204103857,0.4424000150475723,0.2392031446866111,null,4.710246298301589,4.710246298301589,3.972569006755193,3.5447359484728995,3.9253238093854304,4.0839068912846015,3.9703128267599377,"N/A",3.2322160863264835,3.5,10]
[null,1.25,0.6102356459260091,0.5926758300276975,0.5046925006430438,0.5209064912352808,0.6226800439228495,0.6235737360130027,0.7403320921799265,0.39125865341672206,null,3.6089702677242794,3.6089702677242794,2.9652261351537756,2.628363497566429,2.8839113701607246,3.0595415726035124,3.0496481544308778,3.6175784227296126,2.0950811813379984,3,9]
[null,1.5,0.8305985180659571,0.8100907038781475,0.6980911219065856,0.7579700941198294,0.8451065148654457,0.8080540215816209,0.9925782066899844,0.6718565006068302,null,2.38991689896259,2.38991689896259,1.9155660298450068,1.6803910684733172,2.0027162292782807,1.9851310990468305,1.9915167196895598,2.4056947780687397,1.4812089231742163,2.5,8]
[null,2,1.3690532895540695,1.3426879309388666,1.1726525165541903,1.333520617562319,1.390330146773922,1.3243847067762464,1.600642908223456,0.9076274703283533,null,1.3690532895540695,1.3690532895540695,1.3426879309388666,1.1726525165541903,1.333520617562319,1.390330146773922,1.3243847067762464,1.600642908223456,0.9076274703283533,2,7]
[null,2.5,2.38991689896259,1.9155660298450068,1.6803910684733172,2.0027162292782807,1.9851310990468305,1.9915167196895598,2.4056947780687397,1.4812089231742163,null,0.8305985180659571,0.8305985180659571,0.8100907038781475,0.6980911219065856,0.7579700941198294,0.8451065148654457,0.8080540215816209,0.9925782066899844,0.6718565006068302,1.5,6]
[null,3,3.6089702677242794,2.9652261351537756,2.628363497566429,2.8839113701607246,3.0595415726035124,3.0496481544308778,3.6175784227296126,2.0950811813379984,null,0.6102356459260091,0.6102356459260091,0.5926758300276975,0.5046925006430438,0.5209064912352808,0.6226800439228495,0.6235737360130027,0.7403320921799265,0.39125865341672206,1.25,5]
[null,3.5,4.710246298301589,3.972569006755193,3.5447359484728995,3.9253238093854304,4.0839068912846015,3.9703128267599377,"N/A",3.2322160863264835,null,0.3526065506262479,0.3526065506262479,0.33928928878803905,0.2807314684169256,0.3333801543905798,0.3620811607810159,0.3559759204103857,0.4424000150475723,0.2392031446866111,1,4]
[null,4,6.018901191161188,5.121827875143834,4.5930441402182565,5.126953546952399,5.25592847211792,5.178351256260595,5.980078617165279,4.318253849658459,null,0.21756740071847194,0.21756740071847194,0.20713405025042392,0.1670374282980959,0.21756740071847194,0.22395045788442772,0.2207473936559692,0.26535188951445515,0.13958131031577908,0.75,3]
[null,5,0,8.062216483839398,7.284703724536972,"N/A",8.24648976865856,"N/A",9.274787140275564,"N/A",null,0.12397101850369575,0.12397101850369575,0.11612677957685856,0.08865656247228763,0.12920724024811756,0.12798926834611968,0.12798926834611968,"N/A",0,0.5,2]
[null,6,0,11.655155088256953,10.443822591102379,"N/A",11.896021929369551,"N/A",13.268948311893745,"N/A",null,"N/A","N/A","N/A","N/A",0.04632466863277365,"N/A",0.07666617048114388,"N/A","N/A",0.375,1]

{"sheet":"Voltage Drop NEC Table 9","index":20,"n_rows":58,"n_cols":26,"rows_kept":58,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[]
[null,"XL (Reactance) for All Wires",null,"Alternating-Current Resistance for Uncoated Copper Wires",null,null,"Alternating-Current Resistance for Aluminum Wires",null,null,"Effective Z at 0.85 PF for Uncoated Copper Wires",null,null,"Effective Z at 0.85 PF for Uncoated Aluminum Wires"]
["Size","PVC, Aluminum Conduits","Steel Conduit","PVC Conduit","Aluminum Conduit","Steel Conduit","PVC Conduit","Aluminum Conduit","Steel Conduit","PVC Conduit","Aluminum Conduit","Steel Conduit","PVC Conduit","Aluminum Conduit","Steel Conduit",1]
["14 Sol",0.058,0.073,3.1,3.1,3.1,"-","-","-",2.7,2.7,2.7,"-","-","-",2]
["12 Sol",0.054,0.068,2,2,2,3.2,3.2,3.2,1.7,1.7,1.7,2.8,2.8,2.8,3]
["10 Sol",0.05,0.063,1.2,1.2,1.2,2,2,2,1.1,1.1,1.1,1.8,1.8,1.8,4]
["14 Str",0.058,0.073,3.1,3.1,3.1,"-","-","-",2.7,2.7,2.7,"-","-","-",5,null,null,null,"CU","ALX","ALT"]
["12 Str",0.054,0.068,2,2,2,3.2,3.2,3.2,1.7,1.7,1.7,2.8,2.8,2.8,6,null,null,"ST",3,6,6]
["10 Str",0.05,0.063,1.2,1.2,1.2,2,2,2,1.1,1.1,1.1,1.8,1.8,1.8,7,null,null,"PVC",1,4,4]
["8",0.052,0.065,0.78,0.78,0.78,1.3,1.3,1.3,0.69,0.69,0.7,1.1,1.1,1.1,8,null,null,"PVC",1,4,4]
["6",0.051,0.064,0.49,0.49,0.49,0.81,0.81,0.81,0.44,0.45,0.45,0.71,0.72,0.72,9,null,null,"AL",2,5,5]
["4",0.048,0.06,0.31,0.31,0.31,0.51,0.51,0.51,0.29,0.29,0.3,0.46,0.46,0.46,10,null,null,"ST",3,6,6]
["3",0.047,0.059,0.25,0.25,0.25,0.4,0.41,0.4,0.23,0.24,0.24,0.37,0.37,0.37,11,null,null,"AL",2,5,5]
["2",0.045,0.057,0.19,0.2,0.2,0.32,0.32,0.32,0.19,0.19,0.2,0.3,0.3,0.3,12,null,null,"PVC",1,4,4]
["1",0.046,0.057,0.15,0.16,0.16,0.25,0.26,0.25,0.16,0.16,0.16,0.24,0.24,0.25,13,null,null,"ST",3,6,6]
["1/0",0.044,0.055,0.12,0.13,0.12,0.2,0.21,0.2,0.13,0.13,0.13,0.19,0.2,0.2,14]
["2/0",0.043,0.054,0.1,0.1,0.1,0.16,0.16,0.16,0.11,0.11,0.11,0.16,0.16,0.16,15,null,null,"Resistance"]
["3/0",0.042,0.052,0.077,0.082,0.079,0.13,0.13,0.13,0.088,0.092,0.094,0.13,0.13,0.14,16,null,null,5]
["4/0",0.041,0.051,0.062,0.067,0.063,0.1,0.11,0.1,0.074,0.078,0.08,0.11,0.11,0.11,17,null,null,"SCT","CX","CUSE","SAT","AX","AUSE"]
["250",0.041,0.052,0.052,0.057,0.054,0.085,0.09,0.086,0.066,0.07,0.073,0.094,0.098,0.1,18,null,null,3,3,3,6,6,6]
["300",0.041,0.051,0.044,0.049,0.045,0.071,0.076,0.072,0.059,0.063,0.065,0.082,0.086,0.088,19]
["350",0.04,0.05,0.038,0.043,0.039,0.061,0.066,0.063,0.053,0.058,0.06,0.073,0.077,0.08,20]
["400",0.04,0.049,0.033,0.038,0.035,0.054,0.059,0.055,0.049,0.053,0.056,0.066,0.071,0.073,21]
["500",0.039,0.048,0.027,0.032,0.029,0.043,0.048,0.045,0.043,0.048,0.05,0.057,0.061,0.064,22,null,null,"Reactance"]
["600",0.039,0.048,0.023,0.028,0.025,0.036,0.041,0.038,0.04,0.044,0.047,0.051,0.055,0.058,23,null,null,2,{"$nulls":6},2]
["750",0.038,0.048,0.019,0.024,0.021,0.029,0.034,0.031,0.036,0.04,0.043,0.045,0.049,0.052,24,null,null,1,2,3,4,5,6,7,8]
["1000",0.037,0.046,0.015,0.019,0.018,0.023,0.027,0.025,0.032,0.036,0.04,0.039,0.042,0.046,25,null,null,"EMT","PVC 40","PVC 80","Flex FMC","GRC","Flex LFMC","Flex LFNC-B","IMC"]
["900",0.037,0.047,0.016,0.021,0.019,0.025,0.029,0.027,0.033,0.037,0.041,0.041,0.044,0.047,26,null,null,2,1,1,2,2,1,1,2]
[null,"supplied by Tim Andres 6-14-13",{"$nulls":16},2,0,0,2,2,2,0,2]
[]
[{"$nulls":18},"Conductor Index",null,null,null,"1"]
[{"$nulls":18},"CU","CU","AL","AL"]
[{"$nulls":18},"1",null,null,"1"]
[{"$nulls":18},"2","14 Sol","N/A","2"]
[{"$nulls":18},"3","12 Sol","N/A","3"]
[{"$nulls":18},"4","10 Sol","N/A","4"]
[{"$nulls":18},"5","14 Str","N/A","5"]
[{"$nulls":18},"6","12 Str","N/A","6"]
[{"$nulls":18},"7","10 Str","N/A","7"]
[{"$nulls":18},"8","8",6,"9"]
[{"$nulls":18},"9","6",4,"10"]
["Voltage Drop",null,"Single","Three",{"$nulls":14},"10","4",2,"12"]
[null,null,"Phase","Phase",{"$nulls":14},"11","3",1,"13"]
["E","L-L Volts",120,480,{"$nulls":14},"12","2","1/0","14"]
["I","Amps",0,0,{"$nulls":14},"13","1","2/0","15"]
["l","Length",0,0,{"$nulls":14},"14","1/0","3/0","16"]
["R","Resistance","Steel Conduit","Steel Conduit",{"$nulls":14},"15","2/0","4/0","17"]
["X","Reactance","Steel Conduit","Steel Conduit","COSq","SINq",{"$nulls":12},"16","3/0",250,"18"]
["P","Power Factor",0.8,0.8,0.8,0.5999999999999999,{"$nulls":12},"17","4/0","300","19"]
[null,"Volatage Drop",0,0,{"$nulls":14},"18","250","350","20"]
[null,"%",0,0,{"$nulls":14},"19","300","400","21"]
["3 Phase","(I*((COS(P)*R)/1000+(X*SIN(P)/1000)*l)1.732",{"$nulls":16},"20","350","500","22"]
["1 Phase","(I*((COS(P)*R)/1000+(X*SIN(P)/1000)*l)2",{"$nulls":16},"21","400","600","23"]
[{"$nulls":18},"22","500","750","24"]
[{"$nulls":18},"23","600","900","26"]
[{"$nulls":18},"24","750","1000","25"]
[{"$nulls":18},25,"1000","N/A",25]

{"sheet":"Jackets","index":21,"n_rows":45,"n_cols":22,"rows_kept":45,"cut":false,"hidden":true,"merged":[[0,0,0,21],[1,1,2,1],[1,2,2,2],[1,3,2,3],[1,4,2,4],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,20,2,20],[1,21,2,21],[1,10,2,10],[1,11,2,11],[1,12,2,12],[1,13,2,13],[19,2,21,2],[19,3,21,3],[19,4,21,4],[1,18,2,18],[1,19,2,19],[19,6,21,6],[19,5,21,5],[1,14,2,14],[1,15,2,15],[1,16,2,16],[1,17,2,17],[18,0,18,4]],"flags":["formulas_cached_only"]}
["Jacket Property Comparisons"]
[null,"Notes"," Minimum Installation Temp","Tensil Strength (min)","Elongitation (min)","Specific Gravity","Flexability",null,"Abrasion Resistance","Ozone Resistance","Flame Resistance","Moisture Resistance",null,"Acid Resistance","Alkali Resistance","Organic Solvent Resistance","Hydraulic Fluid Resistance",null,"Motor / Crude OILS","Gasoline Kerosene","Alcohol","Hydrocarbons (Halogenated)"]
[]
[null,null,"C (F)","PSI","%","Rel*","Rel*",null,"Rel*","Rel*","Rel*","Rel*",null,"Rel*","Rel*","Rel*","Rel*",null,"Rel*","Rel*","Rel*","Rel*"]
["Jacket type"]
["PVC",null,-10,1500,100,1.43,"Fair",null,"Good","Good","Fair","Good",null,"Good","Good","Fair","Good",null,"Good","Good","Fair","Poor"]
["SIMpull PVC","Exclusive to Southwire"]
["PE",null,-40,1400,350,0.93,"Poor",null,"Good","Good","Poor","Good",null,"Good","Good","Fair","Poor",null,"Fair","Poor","Fair","Poor"]
["CSPE  (Hypalon)","No longer made",-20,1200,200,1.54,"Good",null,"Good","Good","Good","Good",null,"Good","Good","Good","Good",null,"Good","Good","Good","Fair"]
["CPE (PO)",null,-40,1560,420,1.28,"Fair",null,"Good","Good","Good","Good",null,"Good","Good","Good","Good",null,"Good","Good","Good","Poor"]
["CPE (XLP)"]
["SOLONON (LSZH-PO)","Exclusive to Southwire",-20,2000,160,1.5,"Fair",null,"Good","Good","Good","Good",null,"Good","Good","Fair","Good",null,"Good","Good","Good","Poor"]
["SOLONON (LSZH-XLP)","Exclusive to Southwire"]
["SIMpull SOLONON ","Exclusive to Southwire"]
["Neoprene","Not offered by Southwire"]
[]
["Rel* = Relative among materials listed"]
["Source  PCM 5-2"]
["Coefficient of Friction (COF) in Duct"]
[null,null,"Steel or Aluminum","PVC","Fiber (Orangeburg) (Nocrete)","ASB          Asbestos Cement (Transite, Korduct)","Cable Tray"]
[]
[null,"Notes"]
["Jacket type"]
["PVC",null,0.4,0.35,0.5,0.5,0.15]
["SIMpull PVC","Exclusive to Southwire",0.2,0.2]
["PE",null,0.35,0.35,0.5,0.5,0.15]
["CSPE (Hypalon)","No longer made",0.5,0.5,0.7,0.6]
["CPE (PO)",null,0.5,0.5,0.7,0.6,0.15]
["CPE (XLP)"]
["SOLONON (LSZH-PO)","Exclusive to Southwire",0.35,0.35,0.5,0.5,0.15]
["SOLONON (LSZH-XLP)","Exclusive to Southwire",{"$nulls":4},0.15]
["SIMpull SOLONON ","Exclusive to Southwire",{"$nulls":4},0.15]
["Source PCM 7-14",{"$nulls":5},"Per Paul White 12-8-09"]
[]
[]
[]
["Jacket Definations:"]
["PVC","Polyvinal Choloride (thermoplastic)"]
["SIMpull","No lube required for installation in conduit.  Reduced COF."]
["CPE","Chlorinated Polyethylene"]
["CSPE (no longer made)","Chlorosulfinated???? Polyethylene (thermoset) DuPont tradename is Hypalon"]
["PO","Polyolefin???? (thermoplastic)"]
["XLP","Cross linked Polyethylene (thermoset)"]
["SOLONON","SOuthwire LOw smoke NON-halogen"]
["LSZH","Low Smoke Zero Halogen"]

{"sheet":"Conductor","index":22,"n_rows":94,"n_cols":159,"rows_kept":94,"cut":false,"hidden":true,"merged":[[109,230,109,236],[94,15,94,21],[88,9,88,11],[149,173,149,179],[150,173,150,179],[149,155,149,161],[150,155,150,161]],"flags":["formulas_cached_only"]}
[]
[null,"Conductor  Size",{"$nulls":4},"Conductor  Size",{"$nulls":4},"Conductor  Size",{"$nulls":4},"Conductor  Size",null,null,null,"Conductor  Size",null,null,null,"Conductor  Size",{"$nulls":5},"Canadian / CEC Verticle support requirements."]
[null,"Copper THHN",{"$nulls":4},"Copper XHHW",{"$nulls":4},"Aluminum XHHW",{"$nulls":4},"Aluminum THHN",null,null,null,"CU MC",null,null,null,"AL MC",{"$nulls":5},"CU","cu  in meters","AL","AL in Meters"]
[null,"Size","Desc","Amps","Size",null,"Size","Desc","Amps",null,null,"Size","Desc","Amps","Size",null,"Size",null,"Amps",null,"Size","Desc","Amps",null,"Size","Desc","Amps",null,null,null,"size",null,"size"]
[null,"14","#14 AWG-15 Amps",15,"14",null,"14","#14 AWG-15 Amps",15,null,null,"8","#8 AWG-40 Amps",40,"8",null,"6","#6 AWG-50 Amps",50,null,"1","#1 AWG-130 Amps",130,null,6,"#6 AWG-50 Amps",50,null,null,null,"14",30]
[null,"12","#12 AWG-20 Amps",20,"12",null,"12","#12 AWG-20 Amps",20,null,null,"6","#6 AWG-50 Amps",50,"6",null,"4","#4 AWG-65 Amps",65,null,"1/0","1/0 AWG-150 Amps",150,null,4,"#4 AWG-65 Amps",65,null,null,null,"12",30]
[null,"10","#10 AWG-30 Amps",30,"10",null,"10","#10 AWG-30 Amps",30,null,null,"4","#4 AWG-65 Amps",65,"4",null,"2","#2 AWG-90 Amps",90,null,"2/0","2/0 AWG-175 Amps",175,null,2,"#2 AWG-90 Amps",90,null,null,null,"10",30]
[null,"8","#8 AWG-50 Amps",50,"8",null,"8","#8 AWG-50 Amps",50,null,null,"2","#2 AWG-90 Amps",90,"2",null,"1","#1 AWG-100 Amps",100,null,"3/0","3/0 AWG-200 Amps",200,null,1,"#1 AWG-100 Amps",100,null,null,null,"8",30,"8",30]
[null,"6","#6 AWG-65 Amps",65,"6",null,"6","#6 AWG-65 Amps",65,null,null,"1","#1 AWG-100 Amps",100,"1",null,"1/0","1/0 AWG-120 Amps",120,null,"4/0","4/0 AWG-230 Amps",230,null,"1/0","1/0 AWG-120 Amps",120,null,null,null,"6",30,"6",60]
[null,"4","#4 AWG-85 Amps",85,"4",null,"4","#4 AWG-85 Amps",85,null,null,"1/0","1/0 AWG-120 Amps",120,"1/0",null,"2/0","2/0 AWG-135 Amps",135,null,"250","250 KCM-255 Amps",255,null,"2/0","2/0 AWG-135 Amps",135,null,null,null,"4",30,"4",60]
[null,"3","#3 AWG-100 Amps",100,"3",null,"2","#2 AWG-115 Amps",115,null,null,"2/0","2/0 AWG-135 Amps",135,"2/0",null,"3/0","3/0 AWG-155 Amps",155,null,"350","350 KCM-310 Amps",310,null,"3/0","3/0 AWG-155 Amps",155,null,null,null,"2",30,"2",60]
[null,"2","#2 AWG-115 Amps",115,"2",null,"1","#1 AWG-130 Amps",130,null,null,"3/0","3/0 AWG-155 Amps",155,"3/0",null,"4/0","4/0 AWG-180 Amps",180,null,"500","500 KCM-380 Amps",380,null,"4/0","4/0 AWG-180 Amps",180,null,null,null,"1",30,"1",60]
[null,"1","#1 AWG-130 Amps",130,"1",null,"1/0","1/0 AWG-150 Amps",150,null,null,"4/0","4/0 AWG-180 Amps",180,"4/0",null,"250","250 KCM-205 Amps",205,null,"600","600 KCM-420 Amps",420,null,"250","250 KCM-205 Amps",205,null,null,null,"1/0",30,"1/0",60]
[null,"1/0","1/0 AWG-150 Amps",150,"1/0",null,"2/0","2/0 AWG-175 Amps",175,null,null,"250","250 KCM-205 Amps",205,"250",null,"300","300 KCM-230 Amps",230,null,"750","750 KCM-475 Amps",475,null,"350","350 KCM-250 Amps",250,null,null,null,"2/0",24,"2/0",55]
[null,"2/0","2/0 AWG-175 Amps",175,"2/0",null,"3/0","3/0 AWG-200 Amps",200,null,null,"300","300 KCM-230 Amps",230,"300",null,"350","350 KCM-250 Amps",250,{"$nulls":5},"500","500 KCM-310 Amps",310,null,null,null,"3/0",24,"3/0",55]
[null,"3/0","3/0 AWG-200 Amps",200,"3/0",null,"4/0","4/0 AWG-230 Amps",230,null,null,"350","350 KCM-250 Amps",250,"350",null,"400","400 KCM-270 Amps",270,{"$nulls":5},"600","600 KCM-340 Amps",340,null,null,null,"4/0",24,"4/0",55]
[null,"4/0","4/0 AWG-230 Amps",230,"4/0",null,"250","250 KCM-255 Amps",255,null,null,"400","400 KCM-270 Amps",270,"400",null,"500","500 KCM-310 Amps",310,{"$nulls":5},"750","750 KCM-385 Amps",385,null,null,null,"250",18,"250",40]
[null,"250","250 KCM-255 Amps",255,"250",null,"300","300 KCM-285 Amps",285,null,null,"500","500 KCM-310 Amps",310,"500",null,"600","600 KCM-340 Amps",340,{"$nulls":5},900,"900 KCM-425 Amps",425,null,null,null,"300",18,"300",40]
[null,"300","300 KCM-285 Amps",285,"300",null,"350","350 KCM-310 Amps",310,null,null,"600","600 KCM-340 Amps",340,"600",null,"700","700 KCM-375 Amps",375,{"$nulls":11},"350",18,"350",40]
[null,"350","350 KCM-310 Amps",310,"350",null,"400","400 KCM-335 Amps",335,null,null,"700","700 KCM-375 Amps",375,"700",null,"750","750 KCM-385 Amps",385,{"$nulls":11},"400",15,"400",35]
[null,"400","400 KCM-335 Amps",335,"400",null,"500","500 KCM-380 Amps",380,null,null,"750","750 KCM-385 Amps",385,"750",null,"1000","1000 KCM-445 Amps",445,{"$nulls":11},"500",15,"500",35]
[null,"500","500 KCM-380 Amps",380,"500",null,"600","600 KCM-420 Amps",420,null,null,"1000","1000 KCM-445 Amps",445,"1000",{"$nulls":15},"600",12,"600",30]
[null,"600","600 KCM-420 Amps",420,"600",null,"700","700 KCM-460 Amps",460,{"$nulls":21},"700",12,"700",30]
[null,"750","750 KCM-475 Amps",475,"750",null,"750","750 KCM-475 Amps",475,{"$nulls":21},"750",12,"750",25]
[null,"1000","1000 KCM-545 Amps",545,"1000",null,"1000","1000 KCM-545 Amps",545,{"$nulls":21},"1000",10,"900",25]
[{"$nulls":22},"Stranding class b 14-#2 =7, 1-4/0 =19, 250 - 500 = 37, 600 - 1000 =61",{"$nulls":9},1000,25]
[{"$nulls":22},"14 - 2 = 19, 1 - 4/0 = 37, 250 -500 = 61, 600 -1000 = 91"]
[]
[{"$nulls":22},"Federal Spec j-30 xxxxx"]
[]
[]
[]
[{"$nulls":16},"Catalog","Catalog","Catalog","PCM 6-31","BWHB 115","PCM 7-11","PCM 7-10","Catalog","PCM 6-6","NEC 300.34","McCardel 4-16-09","PCM 7-32","Mercier Jan 09","Mercier Jan 09","PCM 7-2","Catalog","Catalog","Mercier Jan 09","Catalog","Catalog","Catalog","Catalog","PCM  2-8"]
[]
["Cable 1","OD","Wt/Ft","Amps","Cmil","Cable 2","OD","Wt/Ft","Amps","Cmil","Cable 3","OD","Wt/Ft","Amps","Cmil","SIMpull CU THHN","Cable OD with compressed strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding","SIMpull CU XHHW","Cable OD with compressed strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding","CU USE","Cable OD with compressed strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding","SIMpull AL THHN","Cable OD with compact strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding","SIMpull AL XHHW","Cable OD with compact strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding",null,"Cable OD with compact strand (inches)",null,"Ampacity @ 75 C 310.15(B)(16)","For derating purposes Ampacity @ 90C  310.15(B)(16)","Reisitance  DC @ 75 C per 1000'","CMIL Area of metal","Max pulling stress","CT Rated","Dielectric Constant (SIC)","Phase wire Min bend radius (inches)","Sunlight Resistant","Verticle support requirements are every","COF","Acceptable Megohm readings","Min installation temp","Max temp for dry location","Max temp for wet location","Suggested Max sidewall pressure Lb. / Ft.","UL standard","NEMA","ICEA","RoHS Compliant","Stranding"]
[{"$nulls":17},"wt / ft.",{"$nulls":4},"pounds",{"$nulls":18},"wt / ft.",{"$nulls":4},"pounds",{"$nulls":18},"wt / ft.",{"$nulls":4},"pounds",{"$nulls":18},"wt / ft.",{"$nulls":4},"pounds",{"$nulls":18},"wt / ft.",{"$nulls":4},"pounds",{"$nulls":16},"AL USE",null,"wt / ft.",{"$nulls":4},"pounds"]
["14 Sol",0.102,0.015,15,4110,"14 Sol",0.102,0.015,15,4110,"14 Sol",0.102,0.015,15,4110,"14 Sol",0.102,0.015,15,25,3.07,4110,32.88,"no",8,0.408,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Solid Soft CU","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
["12 Sol",0.119,0.023,20,6530,"12 Sol",0.119,0.023,20,6530,"12 Sol",0.119,0.023,20,6530,"12 Sol",0.119,0.023,20,30,1.93,6530,52.24,"no",8,0.476,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Solid Soft CU","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
["10 Sol",0.15,0.036,30,10380,"10 Sol",0.15,0.036,30,10380,"10 Sol",0.15,0.036,30,10380,"10 Sol",0.15,0.036,30,40,1.21,10380,83.04,"no",8,0.6,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Solid Soft CU","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
["14 str",0.109,0.016,15,4110,"14 str",0.109,0.016,15,4110,"14 str",0.109,0.016,15,4110,"14 str",0.109,0.016,15,25,3.14,4110,32.88,"no",8,0.436,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C","14 str",0.13,0.018,15,25,3.14,4110,32.88,"no","See catalog sheet",0.52,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B","14 str",0.16,0.02,15,25,3.14,4110,32.88,"no",5,0.64,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
["12 str",0.128,0.024,20,6530,"12 str",0.128,0.024,20,6530,"12 str",0.128,0.024,20,6530,"12 str",0.128,0.024,20,30,1.98,6530,52.24,"no",8,0.512,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C","12 str",0.162,0.037,20,30,1.98,6530,52.24,"no","See catalog sheet",0.648,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B","12 str",0.177,0.029,20,30,1.98,6530,52.24,"no",5,0.708,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
["10 str",0.161,0.038,30,10380,"10 str",0.161,0.038,30,10380,"10 str",0.161,0.038,30,10380,"10 str",0.161,0.038,30,40,1.24,10380,83.04,"no",8,0.644,"no","100 ft.",0.35,"50 M'ohms - infinity ","-10C (14F)","90 C","75 C",500,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C","10 str",0.171,0.04,30,40,1.24,10380,83.04,"no","See catalog sheet",0.684,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B","10 str",0.201,0.042,30,40,1.24,10380,83.04,"no",5,0.804,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","N/A",{"$nulls":23},8,0.227,0.03,40,45,1.28,16510,99.06,"no",5,0.908,"no","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",8,0.257,0.036,40,45,1.28,16510,99.06,"no",5,1.028,"no","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[8,0.213,0.063,50,16510,8,0.213,0.063,50,16510,8,0.213,0.063,50,16510,8,0.213,0.063,50,55,0.778,16510,132.08,"no",8,0.852,"no","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C",8,0.232,0.065,50,55,0.778,16510,132.08,"no","See catalog sheet",0.928,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",8,0.256,0.068,50,55,0.778,16510,132.08,"no",5,1.024,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B",6,0.239,0.038,50,55,0.808,26240,157.44,"no",8,0.956,"no","200 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",6,0.262,0.042,50,55,0.808,26240,157.44,"no",5,1.048,"no","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",6,0.292,0.049,50,55,0.808,26240,157.44,"no",5,1.168,"no","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[6,0.249,0.095,65,26240,6,0.249,0.095,65,26240,6,0.249,0.095,65,26240,6,0.249,0.095,65,75,0.491,26240,209.92000000000002,"no",8,0.996,"no","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C",6,0.268,0.096,65,75,0.491,26240,209.92000000000002,"no","See catalog sheet",1.072,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",6,0.294,0.101,65,75,0.491,26240,209.92000000000002,"no",5,1.176,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B",4,0.305,0.062,65,75,0.508,41740,250.44,"no",8,1.22,"no","200 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",4,0.306,0.058,65,75,0.508,41740,250.44,"no",5,1.224,"no","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",4,0.336,0.065,65,75,0.508,41740,250.44,"no",5,1.344,"no","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[4,0.318,0.152,85,41740,4,0.318,0.152,85,41740,4,0.318,0.152,85,41740,4,0.318,0.152,85,95,0.308,41740,333.92,"no",8,1.272,"no","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C",4,0.311,0.147,85,95,0.308,41740,333.92,"no","See catalog sheet",1.244,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",4,0.341,0.154,85,95,0.308,41740,333.92,"no",5,1.364,"no","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B",2,0.36,0.09,90,100,0.319,66360,398.16,"no",8,1.44,"Black only","200 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",2,0.361,0.086,90,100,0.319,66360,398.16,"no",5,1.444,"blk only","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",2,0.391,0.094,90,100,0.319,66360,398.16,"no",5,1.564,"blk only","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[3,0.346,0.189,100,52620,3,0.346,0.189,100,52620,3,0.346,0.189,100,52620,3,0.346,0.189,100,115,0.245,52620,420.96000000000004,"no",8,1.384,"no","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C",3,0.337,0.183,100,115,0.245,52620,420.96000000000004,"no","See catalog sheet",1.348,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",3,"N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A","50 M'ohms - infinity ","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N/A",null,1,0.413,0.117,100,115,0.253,83690,502.14,"no",8,1.652,"Black only","200 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",1,0.412,0.11,100,115,0.253,83690,502.14,"no",5,1.648,"blk only","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",1,0.462,0.126,100,115,0.253,83690,502.14,"no",5,1.848,"blk only","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[2,0.378,0.234,115,66360,2,0.378,0.234,115,66360,2,0.378,0.234,115,66360,2,0.378,0.234,115,130,0.194,66360,530.88,"no",8,1.512,"black only","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class C",2,0.367,0.227,115,130,0.194,66360,530.88,"no","See catalog sheet",1.468,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",2,0.397,0.235,115,130,0.194,66360,530.88,"no",5,1.588,"blk only","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","1/0",0.45,0.141,120,135,0.201,105600,633.6,"yes",8,1.8,"yes all colors","200 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","1/0",0.449,0.134,120,135,0.201,105600,633.6,"no",5,1.796,"blk only","200 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","1/0",0.499,0.151,120,135,0.201,105600,633.6,"no",5,1.996,"blk only","200 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[1,0.435,0.299,130,83690,1,0.435,0.299,130,83690,1,0.435,0.299,130,83690,1,0.435,0.299,130,145,0.154,83690,669.52,"no",8,1.74,"black only","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B",1,0.435,0.291,130,145,0.154,83690,669.52,"no","See catalog sheet",1.74,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000," 44 & 1581","WC 70","S 95 658","no","Compressed Soft CU Class B",1,0.484,0.309,130,145,0.154,83690,669.52,"no",5,1.936,"blk only","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",500,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","2/0",0.49,0.172,135,150,0.159,133100,798.6,"yes",8,1.96,"yes all colors","180 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","2/0",0.489,0.163,135,150,0.159,133100,798.6,"no",5,1.956,"blk only","180 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","2/0",0.539,0.182,135,150,0.159,133100,798.6,"no",5,2.156,"blk only","180 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["1/0",0.474,0.372,150,105600,"1/0",0.474,0.372,150,105600,"1/0",0.474,0.372,150,105600,"1/0",0.474,0.372,150,170,0.122,105600,844.8000000000001,"yes",8,1.896,"yes all colors","100 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","1/0",0.477,0.363,150,170,0.122,105600,844.8000000000001,"Yes","See catalog sheet",1.908,"yes all colors","100 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","1/0",0.52,0.379,150,170,0.122,105600,844.8000000000001,"no",5,2.08,"blk only","100 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","3/0",0.537,0.21,155,175,0.126,167800,1006.8000000000001,"yes",8,2.148,"yes all colors","180 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","3/0",0.536,0.2,155,175,0.126,167800,1006.8000000000001,"no",5,2.144,"blk only","180 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","3/0",0.586,0.221,155,175,0.126,167800,1006.8000000000001,"no",5,2.344,"blk only","180 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["2/0",0.518,0.462,175,133100,"2/0",0.518,0.462,175,133100,"2/0",0.518,0.462,175,133100,"2/0",0.518,0.462,175,195,0.0967,133100,1064.8,"yes",8,2.072,"yes all colors","80 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","2/0",0.521,0.453,175,195,0.0967,133100,1064.8,"Yes","See catalog sheet",2.084,"yes all colors","80 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","2/0",0.557,0.472,175,195,0.0967,133100,1064.8,"no",5,2.228,"blk only","80 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","4/0",0.589,0.257,180,205,0.1,211600,1269.6000000000001,"yes",8,2.356,"yes all colors","180 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","4/0",0.588,0.247,180,205,0.1,211600,1269.6000000000001,"no",5,2.352,"blk only","180 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","4/0",0.638,0.269,180,205,0.1,211600,1269.6000000000001,"no",5,2.552,"blk only","180 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["3/0",0.568,0.575,200,167800,"3/0",0.568,0.575,200,167800,"3/0",0.568,0.575,200,167800,"3/0",0.568,0.575,200,225,0.0766,167800,1342.4,"yes",8,2.272,"yes all colors","80 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","3/0",0.571,0.565,200,225,0.0766,167800,1342.4,"Yes","See catalog sheet",2.284,"yes all colors","80 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","3/0",0.617,0.5863,200,225,0.0766,167800,1342.4,"no",5,2.468,"blk only","80 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B",250,0.656,0.31,205,230,0.0847,250000,1500,"yes",8,2.624,"yes all colors","135 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",250,0.653,0.296,205,230,0.0847,250000,1500,"no",5,2.612,"blk only","135 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",250,0.713,0.326,205,230,0.0847,250000,1500,"no",5,2.852,"blk only","135 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["4/0",0.624,0.718,230,211600,"4/0",0.624,0.718,230,211600,"4/0",0.624,0.718,230,211600,"4/0",0.624,0.718,230,260,0.0608,211600,1692.8,"yes",8,2.496,"yes all colors","80 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","4/0",0.627,0.706,230,260,0.0608,211600,1692.8,"Yes","See catalog sheet",2.508,"yes all colors","80 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","4/0",0.673,0.729,230,260,0.0608,211600,1692.8,"no",5,2.692,"blk only","80 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","300",0.706,0.365,230,260,0.0707,300000,1800,"yes",8,2.824,"yes all colors","135 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","300",0.703,0.349,230,260,0.0707,300000,1800,"no",5,2.812,"blk only","135 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","300",0.763,0.381,230,260,0.0707,300000,1800,"no",5,3.052,"blk only","135 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[250,0.694,0.851,255,250000,250,0.694,0.851,255,250000,250,0.694,0.851,255,250000,250,0.694,0.851,255,290,0.0515,250000,2000,"yes",8,2.776,"yes all colors","60 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B",250,0.695,0.835,255,290,0.0515,250000,2000,"Yes","See catalog sheet",2.78,"yes all colors","60 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B",250,0.748,0.863,255,290,0.0515,250000,2000,"no",5,2.992,"blk only","60 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","350",0.752,0.418,250,280,0.0605,350000,2100,"yes",8,3.008,"yes all colors","135 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","350",0.749,0.401,250,280,0.0605,350000,2100,"no",5,2.996,"blk only","135 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","350",0.809,0.435,250,280,0.0605,350000,2100,"no",5,3.236,"blk only","135 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["300",0.747,1.012,285,300000,"300",0.747,1.012,285,300000,"300",0.747,1.012,285,300000,"300",0.747,1.012,285,320,0.0429,300000,2400,"yes",8,2.988,"yes all colors","60 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","300",0.748,0.995,285,320,0.0429,300000,2400,"Yes","See catalog sheet",2.992,"yes all colors","60 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","300",0.804,1.029,285,320,0.0429,300000,2400,"no",5,3.216,"blk only","60 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","400",0.795,0.471,270,305,0.0529,400000,2400,"yes",8,3.18,"yes all colors","120 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","400",0.792,0.452,270,305,0.0529,400000,2400,"no",5,3.168,"blk only","120 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","400",0.852,0.488,270,305,0.0529,400000,2400,"no",5,3.408,"blk only","120 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["350",0.797,1.174,310,350000,"350",0.797,1.174,310,350000,"350",0.797,1.174,310,350000,"350",0.797,1.174,310,350,0.0367,350000,2800,"yes",8,3.188,"yes all colors","60 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","350",0.798,1.155,310,350,0.0367,350000,2800,"Yes","See catalog sheet",3.192,"yes all colors","60 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","350",0.854,1.191,310,350,0.0367,350000,2800,"no",5,3.416,"blk only","60 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","500",0.872,0.576,310,350,0.0424,500000,3000,"yes",8,3.488,"yes all colors","120 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","500",0.869,0.556,310,350,0.0424,500000,3000,"no",5,3.476,"blk only","120 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","500",0.929,0.595,310,350,0.0424,500000,3000,"no",5,3.716,"blk only","120 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["400",0.842,1.334,335,400000,"400",0.842,1.334,335,400000,"400",0.842,1.334,335,400000,"400",0.842,1.334,335,380,0.0321,400000,3200,"yes",8,3.368,"yes all colors","50 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","400",0.843,1.314,335,380,0.0321,400000,3200,"Yes","See catalog sheet",3.372,"yes all colors","50 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","400",0.899,1.352,335,380,0.0321,400000,3200,"no",5,3.596,"blk only","50 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","600",0.971,0.7,340,385,0.0353,600000,3600,"yes",8,3.884,"yes all colors","95 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","600",0.976,0.679,340,385,0.0353,600000,3600,"no",5,3.904,"blk only","95 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","N/A",null,null,340,385]
["500",0.926,1.655,380,500000,"500",0.926,1.655,380,500000,"500",0.926,1.655,380,500000,"500",0.926,1.655,380,430,0.0258,500000,4000,"yes",8,3.704,"yes all colors","50 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","500",0.927,1.633,380,430,0.0258,500000,4000,"Yes","See catalog sheet",3.708,"yes all colors","50 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","500",0.983,1.674,380,430,0.0258,500000,4000,"no",5,3.932,"blk only","50 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","750",1.066,0.856,385,435,0.0282,750000,4500,"yes",8,5.33,"yes all colors","95 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","750",1.071,0.833,385,435,0.0282,750000,4500,"no",5,5.3549999999999995,"blk only","95 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","750",1.131,0.881,385,435,0.0282,750000,4500,"no",5,5.655,"blk only","95 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["600",1.024,1.987,420,600000,"600",1.024,1.987,420,600000,"600",1.024,1.987,420,600000,"600",1.024,1.987,420,475,0.0214,600000,4800,"yes",8,5.12,"yes all colors","40 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","600",1.033,1.965,420,475,0.0214,600000,4800,"Yes","See catalog sheet",5.164999999999999,"yes all colors","40 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","600",1.089,2.012,420,475,0.0214,600000,4800,"no",5,5.445,"blk only","40 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","900",1.139,1.013,425,480,0.0235,900000,5400,"yes",8,5.695,"yes all colors","85 ft",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","900",1.162,0.987,425,480,0.0235,900000,5400,"no",5,6.9719999999999995,"blk only","85 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","N/A",null,null,425,480]
["750",1.126,2.462,475,750000,"750",1.126,2.462,475,750000,"750",1.126,2.462,475,750000,"750",1.126,2.462,475,535,0.0171,750000,6000,"yes",8,5.629999999999999,"yes all colors","40 ft.",0.14,"50 M'ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","750",1.135,2.44,475,535,0.0171,750000,6000,"Yes","See catalog sheet",5.675,"yes all colors","40 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","750",1.191,2.492,475,535,0.0171,750000,6000,"no",5,5.955,"blk only","40 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","1000",1.218,1.117,445,500,0.0212,1000000,6000,"yes",8,6.09,"yes all colors","85 ft",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B","1000",1.223,1.09,445,500,0.0212,1000000,6000,"no",5,6.115,"blk only","85 ft",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B","1000",1.283,1.145,445,500,0.0212,1000000,6000,"no",5,6.414999999999999,"blk only","85 ft",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
["1000",1.275,3.255,545,1000000,"1000",1.275,3.255,545,1000000,"1000",1.275,3.255,545,1000000,"1000",1.275,3.255,545,615,0.0129,1000000,8000,"yes",8,6.375,"yes all colors","35 ft.",0.14,"50 ohms - infinity ","-10C (14F)","90 C","90 C",1000,"83, 1581, 1063","N / A","no","yes","Compressed Soft CU Class B","1000",1.284,3.229,545,615,0.0129,1000000,8000,"Yes","See catalog sheet",6.42,"yes all colors","35 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 1581, 1685 ","WC 70","S 95 658","no","Compressed Soft CU Class B","1000",1.34,3.288,545,615,0.0129,1000000,8000,"no",5,6.7,"blk only","35 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95 658","no","Compressed Soft Cu Class B","N/A",{"$nulls":23},"N/A",{"$nulls":23},"N/A"]
[{"$nulls":87},700,1.035,0.804,375,425,0.0303,700000,4200,"yes",0.8,4.14,"Yes all colors","95 ft.",0.14,"50 M'ohms  - infinity ","-10C (14F)","90 C","90 C",1000,83,"no","no","yes","Compact AA 8000 Series Alloy Class B",700,1.04,0.787,375,425,0.0303,700000,4200,"no",5,4.16,"blk only","95 ft.",0.16,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,44,"WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B",700,1100,0.829,375,425,0.0303,700000,4200,"no",5,5500,"blk only","95 ft.",0.35,"50 M'ohms - infinity ","-40C (-40F)","90 C","90 C",1000,"44, 854","WC 70","S 95658","no","Compact AA 8000 Series Alloy Class B"]
[]
[{"$nulls":10},"",{"$nulls":6},"GW for Power Cable Calc"]
["Conductor Area",{"$nulls":5},"Conductor Resistance",null,null,"C1","",null,"",null,null,null,"SIMpull CU THHN","Wt. per Ft.","CUXHHW","Wt. per Ft.","CU USE","Wt. per Ft."]
["Size","cmil","inches2","mm2",null,null,0,0,null,"C2","",null,"",null,null,"10 str",0.161,0.038,0.172,0.04,0.201,0.044]
["1",83690,0.06573,42.41,null,null,"14 Sol",3.07,null,"C3","",{"$nulls":4},8,0.213,0.063,0.234,0.066,0.262,0.073]
["1/0",105600,0.08291,53.49,null,null,"12 Sol",1.93,{"$nulls":7},6,0.249,0.095,0.271,0.1,0.297,0.107]
["10",10380,0.00816,5.261,null,null,"10 Sol",1.21,null,0,{"$nulls":5},4,0.318,0.152,0.318,0.15,0.344,0.157]
["1000",1000000,0.7854,506.7,null,null,"14 str",3.14,null,null," and "," and ",null,null,null,2,0.378,0.234,0.376,0.231,0.4,0.24]
["12",6350,0.00513,3.308,null,null,"12 str",1.98,null,null,", "," and ",null,null,null,1,0.435,0.299,0.434,0.292,0.484,0.309]
["14",4110,0.00323,2.082,null,null,"10 str",1.24,{"$nulls":7},"1/0",0.474,0.372,0.473,0.363,0.523,0.381]
["2",66360,0.05212,33.63,null,null,8,0.778,{"$nulls":7},"2/0",0.518,0.462,0.517,0.452,0.567,0.472]
["2/0",133100,0.1045,67.42,null,null,6,0.491,{"$nulls":7},"3/0",0.568,0.575,0.567,0.565,0.617,0.586]
["250",250000,0.1963,126.6,null,null,4,0.308,{"$nulls":7},"4/0",0.624,0.718,0.623,0.706,0.673,0.729]
["3",52620,0.04133,26.66,null,null,3,0.245,{"$nulls":7},250,0.694,0.851,0.691,0.835,0.751,0.867]
["3/0",167800,0.1318,85.03,null,null,2,0.194,{"$nulls":7},"350",0.797,1.174,0.794,1.155,0.854,1.191]
["300",300000,0.2356,152,null,null,1,0.154,{"$nulls":7},"500",0.926,1.655,0.923,1.632,0.983,1.674]
["350",350000,0.2749,177.4,null,null,"1/0",0.122,{"$nulls":7},"600",1.024,1.987,1.029,1.966,1.089,2.012]
["4",41740,0.03278,21.15,null,null,"2/0",0.0967,{"$nulls":7},"750",1.126,2.464,1.131,2.283,1.191,2.492]
["4/0",211600,0.1662,107.2,null,null,"3/0",0.0766,{"$nulls":7},"1000",1.275,3.257,1.28,3.231,1.34,3.289]
["400",400000,0.3142,202.7,null,null,"4/0",0.0608]
["450",450000,0.3534,228,null,null,250,0.0515]
["5",33090,0.02599,16.77,null,null,"300",0.0429]
["500",500000,0.3927,253.4,null,null,"350",0.0367]
["550",550000,0.432,278.7,null,null,"400",0.0321]
["6",26240,0.02061,13.3,null,null,"500",0.0258]
["600",600000,0.4712,304,null,null,"600",0.0214]
["650",650000,0.5105,329.4,null,null,"750",0.0171]
["7",20820,0.01635,10.55,null,null,"1000",0.0129,null,"Special Make item"]
["700",700000,0.5498,354.7]
["750",750000,0.589,380]
["8",16510,0.01297,8.368]
["800",800000,0.6283,405.4]
["900",900000,0.7069,456.1]

{"sheet":"Conductor Aux","index":23,"n_rows":1747,"n_cols":65,"rows_kept":1747,"cut":false,"hidden":true,"merged":[[903,26,904,26],[983,29,984,29],[1644,9,1645,9],[1644,10,1645,10],[1644,11,1645,11],[1644,12,1645,12],[983,24,984,24],[983,25,984,25],[983,26,984,26],[903,22,904,22],[983,21,984,21],[1469,11,1470,11],[1513,12,1514,12],[1557,12,1558,12],[1601,11,1602,11],[1601,12,1602,12],[1601,10,1602,10],[1557,10,1558,10],[1513,10,1514,10],[1513,11,1514,11],[1557,11,1558,11],[1424,11,1425,11],[903,30,904,30],[1644,13,1645,13],[903,28,904,28],[903,29,904,29],[1644,14,1645,14],[903,25,904,25],[903,27,904,27],[983,30,984,30],[903,23,904,23],[903,19,904,19],[983,28,984,28],[903,24,904,24],[1063,14,1064,14],[981,16,981,23],[1384,14,1385,14],[983,14,984,14],[1601,13,1602,13],[1513,13,1514,13],[1557,13,1558,13],[1384,13,1385,13],[1424,13,1425,13],[1469,13,1470,13],[983,27,984,27],[983,23,984,23],[1644,0,1645,0],[983,19,984,19],[864,17,865,17],[864,18,865,18],[864,19,865,19],[983,18,984,18],[983,20,984,20],[982,16,982,23],[903,18,904,18],[1644,7,1645,7],[1644,8,1645,8],[1644,2,1645,2],[1644,3,1645,3],[1644,4,1645,4],[1644,5,1645,5],[1023,14,1024,14],[864,23,865,23],[1644,6,1645,6],[864,20,865,20],[864,21,865,21],[864,22,865,22],[983,22,984,22],[903,20,904,20],[903,21,904,21],[1644,1,1645,1],[784,30,785,30],[824,29,825,29],[824,26,825,26],[824,25,825,25],[864,24,865,24],[864,29,865,29],[864,27,865,27],[824,30,825,30],[864,25,865,25],[784,24,785,24],[784,29,785,29],[864,30,865,30],[824,28,825,28],[824,24,825,24],[864,28,865,28],[864,26,865,26],[824,27,825,27],[784,28,785,28],[784,25,785,25],[784,26,785,26],[784,27,785,27],[584,24,585,24],[584,21,585,21],[584,25,585,25],[544,25,545,25],[584,27,585,27],[544,26,545,26],[544,24,545,24],[544,23,545,23],[584,22,585,22],[584,30,585,30],[584,26,585,26],[584,28,585,28],[584,29,585,29],[464,27,465,27],[504,27,505,27],[544,29,545,29],[504,30,505,30],[504,29,505,29],[544,27,545,27],[464,26,465,26],[424,30,425,30],[544,28,545,28],[464,30,465,30],[424,28,425,28],[424,29,425,29],[544,30,545,30],[464,29,465,29],[464,28,465,28],[504,28,505,28],[424,27,425,27],[424,20,425,20],[424,22,425,22],[424,23,425,23],[424,21,425,21],[424,24,425,24],[424,25,425,25],[424,26,425,26],[424,19,425,19],[504,24,505,24],[504,25,505,25],[504,26,505,26],[464,23,465,23],[464,24,465,24],[464,25,465,25],[464,22,465,22],[424,17,425,17],[504,18,505,18],[903,17,904,17],[584,23,585,23],[784,22,785,22],[784,21,785,21],[424,18,425,18],[983,16,984,16],[424,16,425,16],[464,16,465,16],[504,21,505,21],[464,21,465,21],[464,20,465,20],[584,18,585,18],[584,19,585,19],[544,19,545,19],[464,19,465,19],[464,17,465,17],[464,18,465,18],[504,19,505,19],[504,17,505,17],[501,16,501,23],[584,20,585,20],[504,23,505,23],[784,23,785,23],[824,22,825,22],[541,16,541,23],[504,16,505,16],[504,20,505,20],[544,21,545,21],[544,22,545,22],[504,22,505,22],[544,17,545,17],[544,18,545,18],[824,17,825,17],[824,18,825,18],[824,19,825,19],[784,20,785,20],[784,19,785,19],[784,18,785,18],[824,20,825,20],[824,21,825,21],[824,23,825,23],[864,16,865,16],[544,20,545,20],[584,17,585,17],[784,17,785,17],[1601,14,1602,14],[1424,14,1425,14],[1143,14,1144,14],[1303,14,1304,14],[983,17,984,17],[1469,14,1470,14],[1557,14,1558,14],[544,16,545,16],[824,16,825,16],[1343,14,1344,14],[784,16,785,16],[584,16,585,16],[864,14,865,14],[903,14,904,14],[704,14,705,14],[1513,14,1514,14],[943,14,944,14],[901,16,901,23],[902,16,902,23],[903,16,904,16],[1513,8,1514,8],[1513,9,1514,9],[1557,8,1558,8],[1557,9,1558,9],[1601,8,1602,8],[1601,9,1602,9],[1513,6,1514,6],[1513,7,1514,7],[1557,6,1558,6],[1557,7,1558,7],[1601,6,1602,6],[1601,7,1602,7],[1513,4,1514,4],[1513,5,1514,5],[1557,4,1558,4],[1557,5,1558,5],[1601,4,1602,4],[1601,5,1602,5],[1557,0,1558,0],[1557,1,1558,1],[1557,2,1558,2],[1557,3,1558,3],[1601,0,1602,0],[1601,1,1602,1],[1601,2,1602,2],[1601,3,1602,3],[1513,0,1514,0],[1513,1,1514,1],[1513,2,1514,2],[1513,3,1514,3],[1103,14,1104,14],[1183,14,1184,14],[1223,14,1224,14],[1263,14,1264,14],[1303,9,1304,9],[1343,8,1344,8],[824,14,825,14],[744,14,745,14],[784,14,785,14],[1223,11,1224,11],[1343,10,1344,10],[1343,11,1344,11],[64,14,65,14],[104,14,105,14],[144,14,145,14],[184,14,185,14],[624,14,625,14],[664,14,665,14],[224,14,225,14],[264,14,265,14],[304,14,305,14],[344,14,345,14],[384,14,385,14],[424,14,425,14],[464,14,465,14],[504,14,505,14],[544,14,545,14],[584,14,585,14],[1341,0,1341,6],[1303,0,1304,0],[1384,0,1385,0],[1343,0,1344,0],[1343,9,1344,9],[1343,7,1344,7],[1384,1,1385,1],[1383,0,1383,6],[1303,1,1304,1],[1382,0,1382,6],[1343,4,1344,4],[1342,0,1342,6],[1303,2,1304,2],[1303,8,1304,8],[1343,3,1344,3],[1343,1,1344,1],[1384,8,1385,8],[1384,9,1385,9],[1469,8,1470,8],[1469,10,1470,10],[1424,8,1425,8],[1424,9,1425,9],[1469,9,1470,9],[1384,10,1385,10],[1424,2,1425,2],[1424,3,1425,3],[1424,4,1425,4],[1384,3,1385,3],[1384,4,1385,4],[1469,6,1470,6],[1469,7,1470,7],[1384,7,1385,7],[1424,5,1425,5],[1424,10,1425,10],[1424,6,1425,6],[1424,7,1425,7],[1422,0,1422,6],[1423,0,1423,6],[1424,0,1425,0],[1424,1,1425,1],[1384,11,1385,11],[1384,2,1385,2],[1303,10,1304,10],[1263,11,1264,11],[1103,11,1104,11],[1143,10,1144,10],[1143,11,1144,11],[1183,10,1184,10],[1183,11,1184,11],[1303,11,1304,11],[1223,10,1224,10],[1103,10,1104,10],[1343,5,1344,5],[1303,5,1304,5],[1303,6,1304,6],[1303,3,1304,3],[1384,5,1385,5],[1384,6,1385,6],[1343,2,1344,2],[1303,4,1304,4],[1343,6,1344,6],[1263,9,1264,9],[1263,10,1264,10],[1183,5,1184,5],[64,10,65,10],[224,10,225,10],[144,11,145,11],[184,10,185,10],[64,11,65,11],[224,11,225,11],[104,11,105,11],[104,10,105,10],[344,10,345,10],[264,11,265,11],[1183,9,1184,9],[1183,2,1184,2],[1183,7,1184,7],[464,11,465,11],[384,11,385,11],[544,10,545,10],[584,10,585,10],[864,11,865,11],[903,10,904,10],[1143,2,1144,2],[1182,0,1182,6],[424,10,425,10],[424,11,425,11],[464,10,465,10],[504,10,505,10],[384,10,385,10],[504,11,505,11],[1023,11,1024,11],[1103,8,1104,8],[1143,9,1144,9],[1143,5,1144,5],[1143,6,1144,6],[664,10,665,10],[664,11,665,11],[704,10,705,10],[704,11,705,11],[1103,9,1104,9],[983,9,984,9],[1063,10,1064,10],[943,10,944,10],[983,11,984,11],[1062,0,1062,6],[1103,2,1104,2],[1103,3,1104,3],[1063,4,1064,4],[1063,6,1064,6],[1021,0,1021,6],[1063,5,1064,5],[824,10,825,10],[784,10,785,10],[1143,8,1144,8],[624,11,625,11],[584,11,585,11],[744,11,745,11],[744,10,745,10],[903,9,904,9],[824,9,825,9],[864,9,865,9],[784,11,785,11],[903,11,904,11],[824,11,825,11],[864,10,865,10],[704,9,705,9],[1223,9,1224,9],[1143,0,1144,0],[1143,4,1144,4],[1143,7,1144,7],[1143,3,1144,3],[1103,4,1104,4],[1103,6,1104,6],[1103,5,1104,5],[1103,7,1104,7],[1183,6,1184,6],[1223,2,1224,2],[1223,3,1224,3],[1223,7,1224,7],[1223,8,1224,8],[1223,4,1224,4],[1223,5,1224,5],[1223,1,1224,1],[1143,1,1144,1],[1141,0,1141,6],[1063,7,1064,7],[1103,0,1104,0],[1103,1,1104,1],[1263,6,1264,6],[1263,1,1264,1],[1263,0,1264,0],[1263,2,1264,2],[1223,0,1224,0],[1261,0,1261,7],[1262,0,1262,7],[1302,0,1302,6],[1303,7,1304,7],[1223,6,1224,6],[1263,8,1264,8],[1183,0,1184,0],[1183,1,1184,1],[1263,4,1264,4],[1263,5,1264,5],[1263,3,1264,3],[1183,3,1184,3],[1183,8,1184,8],[1183,4,1184,4],[1263,7,1264,7],[1301,0,1301,7],[1022,0,1022,6],[1063,3,1064,3],[1023,8,1024,8],[1063,9,1064,9],[1023,9,1024,9],[1061,0,1061,6],[1063,0,1064,0],[1063,1,1064,1],[1063,2,1064,2],[1063,8,1064,8],[1023,5,1024,5],[1023,2,1024,2],[1023,3,1024,3],[1023,0,1024,0],[1023,1,1024,1],[1023,6,1024,6],[1023,4,1024,4],[1023,7,1024,7],[943,9,944,9],[982,0,982,7],[981,0,981,7],[943,4,944,4],[983,0,984,0],[983,1,984,1],[983,2,984,2],[983,8,984,8],[983,5,984,5],[983,6,984,6],[943,7,944,7],[983,7,984,7],[983,4,984,4],[983,3,984,3],[943,8,944,8],[943,5,944,5],[943,6,944,6],[943,0,944,0],[943,1,944,1],[943,2,944,2],[943,3,944,3],[903,3,904,3],[903,4,904,4],[903,0,904,0],[903,1,904,1],[903,2,904,2],[903,7,904,7],[864,0,865,0],[864,1,865,1],[864,7,865,7],[864,6,865,6],[864,4,865,4],[864,8,865,8],[864,3,865,3],[864,2,865,2],[864,5,865,5],[903,8,904,8],[903,5,904,5],[903,6,904,6],[824,8,825,8],[824,4,825,4],[824,7,825,7],[824,1,825,1],[824,2,825,2],[824,3,825,3],[824,6,825,6],[902,0,902,7],[901,0,901,7],[704,8,705,8],[744,9,745,9],[744,4,745,4],[784,6,785,6],[664,0,665,0],[824,0,825,0],[784,9,785,9],[784,3,785,3],[784,4,785,4],[784,5,785,5],[824,5,825,5],[744,0,745,0],[784,7,785,7],[784,8,785,8],[744,1,745,1],[744,2,745,2],[744,3,745,3],[744,7,745,7],[744,8,745,8],[784,0,785,0],[784,1,785,1],[744,5,745,5],[744,6,745,6],[784,2,785,2],[661,0,661,6],[662,0,662,6],[704,7,705,7],[704,0,705,0],[704,1,705,1],[704,2,705,2],[664,1,665,1],[664,2,665,2],[664,3,665,3],[704,3,705,3],[704,4,705,4],[704,5,705,5],[704,6,705,6],[624,2,625,2],[664,9,665,9],[664,5,665,5],[664,6,665,6],[664,7,665,7],[664,8,665,8],[664,4,665,4],[584,0,585,0],[624,7,625,7],[624,8,625,8],[624,9,625,9],[624,3,625,3],[624,4,625,4],[624,5,625,5],[624,6,625,6],[624,0,625,0],[624,1,625,1],[584,1,585,1],[584,2,585,2],[584,3,585,3],[584,4,585,4],[584,9,585,9],[584,5,585,5],[584,6,585,6],[584,7,585,7],[584,8,585,8],[544,5,545,5],[544,6,545,6],[464,3,465,3],[464,4,465,4],[464,5,465,5],[464,6,465,6],[544,3,545,3],[544,4,545,4],[504,5,505,5],[504,6,505,6],[544,7,545,7],[544,8,545,8],[464,8,465,8],[424,0,425,0],[464,0,465,0],[504,2,505,2],[541,0,541,7],[464,2,465,2],[501,0,501,7],[504,0,505,0],[504,4,505,4],[384,0,385,0],[384,1,385,1],[424,5,425,5],[424,6,425,6],[424,3,425,3],[384,2,385,2],[384,5,385,5],[384,6,385,6],[424,4,425,4],[384,3,385,3],[424,8,425,8],[384,8,385,8],[344,3,345,3],[344,4,345,4],[344,5,345,5],[384,7,385,7],[344,6,345,6],[304,7,305,7],[344,7,345,7],[344,8,345,8],[384,4,385,4],[144,9,145,9],[184,9,185,9],[184,5,185,5],[184,6,185,6],[184,7,185,7],[184,8,185,8],[144,7,145,7],[144,8,145,8],[184,0,185,0],[144,5,145,5],[144,6,145,6],[184,3,185,3],[184,4,185,4],[184,1,185,1],[184,2,185,2],[62,0,62,3],[104,2,105,2],[104,3,105,3],[104,0,105,0],[64,1,65,1],[101,0,101,3],[102,0,102,4],[104,4,105,4],[64,3,65,3],[64,0,65,0],[64,6,65,6],[64,2,65,2],[64,5,65,5],[1469,4,1470,4],[1469,5,1470,5],[144,4,145,4],[142,0,142,3],[144,0,145,0],[144,1,145,1],[144,2,145,2],[144,3,145,3],[264,4,265,4],[224,5,225,5],[224,6,225,6],[264,3,265,3],[264,5,265,5],[262,0,262,4],[264,0,265,0],[264,6,265,6],[224,4,225,4],[344,0,345,0],[264,1,265,1],[264,2,265,2],[1469,0,1470,0],[1469,1,1470,1],[1469,2,1470,2],[1469,3,1470,3],[141,0,141,3],[104,1,105,1],[1467,0,1467,3],[302,0,302,4],[224,2,225,2],[304,3,305,3],[304,0,305,0],[304,1,305,1],[304,2,305,2],[344,1,345,1],[344,2,345,2],[222,0,222,4],[544,0,545,0],[504,3,505,3],[504,1,505,1],[424,1,425,1],[424,2,425,2],[544,1,545,1],[544,2,545,2],[464,1,465,1],[64,9,65,9],[304,9,305,9],[304,4,305,4],[224,0,225,0],[224,1,225,1],[304,5,305,5],[304,6,305,6],[264,8,265,8],[64,12,65,12],[104,12,105,12],[144,12,145,12],[184,12,185,12],[144,10,145,10],[184,11,185,11],[304,11,305,11],[304,12,305,12],[104,9,105,9],[104,6,105,6],[104,7,105,7],[104,8,105,8],[104,5,105,5],[64,8,65,8],[64,7,65,7],[64,4,65,4],[264,7,265,7],[224,3,225,3],[264,9,265,9],[264,12,265,12],[264,10,265,10],[544,9,545,9],[584,12,585,12],[224,12,225,12],[224,9,225,9],[384,12,385,12],[344,11,345,11],[344,12,345,12],[224,7,225,7],[224,8,225,8],[384,9,385,9],[304,8,305,8],[344,9,345,9],[504,9,505,9],[504,7,505,7],[424,9,425,9],[464,7,465,7],[464,9,465,9],[504,8,505,8],[424,7,425,7],[1343,12,1344,12],[1223,12,1224,12],[1183,12,1184,12],[304,10,305,10],[983,12,984,12],[1023,12,1024,12],[1063,12,1064,12],[424,12,425,12],[784,12,785,12],[504,12,505,12],[544,12,545,12],[903,12,904,12],[943,12,944,12],[1143,12,1144,12],[1103,12,1104,12],[464,12,465,12],[1263,12,1264,12],[744,12,745,12],[943,11,944,11],[1063,11,1064,11],[983,10,984,10],[1023,10,1024,10],[624,10,625,10],[544,11,545,11],[384,13,385,13],[903,13,904,13],[424,13,425,13],[464,13,465,13],[504,13,505,13],[544,13,545,13],[344,13,345,13],[864,12,865,12],[664,13,665,13],[624,12,625,12],[824,12,825,12],[704,12,705,12],[664,12,665,12],[584,13,585,13],[784,13,785,13],[824,13,825,13],[704,13,705,13],[744,13,745,13],[1384,12,1385,12],[1469,12,1470,12],[1424,12,1425,12],[1303,12,1304,12],[1303,13,1304,13],[1263,13,1264,13],[64,13,65,13],[104,13,105,13],[144,13,145,13],[184,13,185,13],[224,13,225,13],[304,13,305,13],[264,13,265,13],[1343,13,1344,13],[864,13,865,13],[943,13,944,13],[983,13,984,13],[1183,13,1184,13],[1223,13,1224,13],[1063,13,1064,13],[1103,13,1104,13],[1143,13,1144,13],[1023,13,1024,13],[624,13,625,13]],"flags":["formulas_cached_only"]}
["CU","CU Amp","AL","AL Amp",null,"Cmil area of Metal","CU Diameter","AL Diameter",null,"Metal",null,null,"CCC",null,null,"Volt",null,null,"Armor",null,null,"Jacket",null,null,"11813",null,"M","C","V","A","J","R","Metal","CCC","Volt","Armor","Jacket","Short Circuit Temp","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Ampacity 1","Ampacity 2","max length","CT Rated","High pot testing","Max Sidewall Pressure","Min Inst Temp","Product#","URL","Short Circuit Factor","COF","# Conductors","Min Bend Radius","Header G","Header H","Shield Short Circuit Factor","No. of Conductors","Cmil (sgl)","Ext Ins Shld Dia (+10)","Metal Area used for tensions","Conductor","Desc"]
[{"$nulls":9},1,"CU",1,1,"1 / C",1,1,"600V RHH RHW USE (XLP) ",1,1,"None",1,1,"None",1,11813,null,1,1,2,1,1,11211,"CU","1/C","600 XHHW","None","None","500",55701799,"66 x 42",1645,"N/A",0.923,430,700,4500,"Yes","N/A","1000","- 40C (-40F)","XHHW/CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45001+CU+1C+XLPE-SIM+XHHW+none+600V+.pdf",0.0719,0.35,1,3.692,"Duct 90C NEC 310.16","In Cable Tray Free Air NEC 392.11 @ 90 C","N/A","1",500000,0,500000,"500","CU 1 / C 600V SIMpull XHHW ( XLP)"]
[null,15,"14 Str","-",null,4110,null,null,null,2,"AL",2,2,"3 / C WG",2,2,"600V XHHW ( XLP)",2,2,"Steel ",2,2,"PVC",2,null,null,1,1,1,1,1,11111,"CU","1/C","600 RHH","None","None","500",89010999,"66 x 42",1693,"N/A",0.983,430,700,4500,"Yes","N/A","1000","- 40C (-40F)","RHH or RHW-2 / CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45003+CU+1C+XLPE+RHW+none+600V+.pdf",0.0719,0.35,1,3.932,"Duct 90C NEC 310.16","In Cable Tray Free Air NEC 392.11","N/A","1",500000,0,500000,"500","CU 1 / C 600V RHH RHW USE (XLP) Non Armored Non Jacketed"]
[null,20,"12 Str",20,null,6530,{"$nulls":6},3,"4 / C WG",3,3,"600V THHN THWN",3,3,"Aluminum (AIA)",3,3,"SIMpull PVC",3,"https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",null,1,1,2,1,2,11212,"CU","1/C","600 XHHW","None","PVC","500",89002299,"66 x 42",1763,"N/A",1.053,430,700,4000,"Yes","N/A","1000","-10C (14F)","XHHW/PVC CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45002+CU+1C+XLPE+XHHW+PVC+600V+.pdf",0.0719,0.35,1,5.265,"Duct 90 C NEC 310.16","In Cable Tray Free Air NEC 318.11 @ 90 C","N/A","1",500000,0,500000,"500","CU 1 / C 600V XHHW ( XLP) Non Armored PVC Jacketed"]
["10 Str",30,"10 Str",30,null,10380,{"$nulls":9},4,"1kV Non Shielded",4,4,"Armor-X (CCA)",4,4,"CPE-PO",4,null,null,1,2,3,1,2,12312,"CU","3/C WG","600 THHN","None","PVC","500",44352399,"92 x 55",5906,"2 bare",2.22,380,430,2000,"Yes","N/A","1000","-10C (14F)","Type TC THHN","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf",0.0529,0.35,3,13.32,"75 C 310.16","90 C 310.16","N/A","3",500000,0,1566360,"500","CU 3 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
["8",50,"8",40,null,16510,{"$nulls":9},5,"2.4 kV Non Shielded",5,5,"Tech 90",5,5,"CPE-XLP",5,null,null,1,3,3,1,2,13312,"CU","4/C WG","600 THHN","None","PVC","500",55251399,"92 x 55",7652,"2 bare",2.455,380,430,1500,"Yes","N/A","1000","-10C (14F)","Type TC THHN","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf",0.0529,0.35,4,14.73,"75 C 310.16","90 C 310.16","N/A","4",500000,0,2066360,"500","CU 4 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
[6,65,6,50,null,26240,{"$nulls":9},6,"5kV 115 Mil EPR 133% CU Tape",6,null,null,null,6,"SOLONON PO",6,null,null,1,2,2,1,2,12212,"CU","3/C WG","600 XHHW","None","PVC","500"," 48-07-23-99","92 x 55",5755,"2 bare",2.214,380,430,2000,"Yes","N/A","1000","-10C (14F)","Type TC XHHW","http://media.industrial.southwire.com/spec/spec45000/SPEC45252+CU+3C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf",0.0719,0.35,3,13.283999999999999,"75 C 310.16","90 C 310.16","N/A","3",500000,0,1566360,"500","CU 3 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
[4,85,4,65,null,41740,{"$nulls":9},7,"15kV 175 Mil EPR 100% CU Tape",7,null,null,null,7,"SOLONON XLP",7,null,null,1,3,2,1,2,13212,"CU","4/C WG","600 XHHW","None","PVC","500",55446999,"92 x 55",7562,"2 bare",2.448,380,430,1500,"Yes","N/A","1000","-10C (14F)","Type TC XHHW","http://media.industrial.southwire.com/spec/spec45000/SPEC45258+CU+4C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf",0.0719,0.35,4,14.687999999999999,"75 C 310.16","90 C 310.16","N/A","4",500000,0,2066360,"500","CU 4 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
["3",{"$nulls":14},8,"15kV 220 Mil EPR 133% CU Tape",8,null,null,null,8,"SOLONON XLP",8,null,null,1,2,2,1,4,12214,"CU","3/C WG","600 XHHW","None","CPE-PO","500",89071099,"78 x 54",5853,"2 bare",2.214,380,430,1500,"Yes","N/A","1000","- 40C (-40F)","Type TC XHHW CPE","http://media.industrial.southwire.com/spec/spec45000/SPEC45255+CU+3C+EPR+XHHW+CPE+600V+W1CUGW.pdf",0.0719,0.5,3,13.283999999999999,"75 C 310.16","90 C 310.16","N/A","3",500000,0,1566360,"500","CU 3 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[2,115,2,90,null,66360,{"$nulls":9},9,"25kV 320 MIL EPR 133% CU Tape",9,{"$nulls":8},1,3,2,1,5,13215,"CU","4/C WG","600 XHHW","None","CPE-PO","500","55-03-91-99","92 x 55",7586,"2 bare",2.448,380,430,1500,"Yes","N/A","1000","- 40C (-40F)","Type TC XHHW/CPE","http://media.industrial.southwire.com/spec/spec45000/SPEC45262+CU+4C+EPR+XHHW+CPE+600V+W1CUGW.pdf",0.0719,0.5,4,14.687999999999999,"75 C 310.16","90 C 310.16","N/A","4",500000,0,2066360,"500","CU 4 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[1,130,1,100,null,83690,{"$nulls":9},10,"28kV 280 MIL EPR 100% CU Tape",10,{"$nulls":8},1,1,5,1,3,11513,"CU","1/C","2.4 KV","None","SIMpull PVC","500","60-73-09-99","78 x 54",2088,"N/A",1.357,470,505,4000,"Yes ","N/A",1000,"-10C (14F)","EFC 09ENS/SIMpull PVC","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf",0.0678,0.2,1,10.856,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,0,500000,"500","CU 1 / C 2.4 kV Non Shielded Non Armored SIMpull-PVC Jacketed"]
["1/0",150,"1/0",120,null,105600,{"$nulls":9},11,"35kV 345 MIL EPR 100% CU Tape",11,{"$nulls":8},1,1,5,1,8,11518,"CU","1/C","2.4 KV","None","SOLONON","500",61117899,"78 x 54",2101,"N/A",1.357,470,505,4000,"YES","N/A",1000,"-40C (-40F)","EFC 09ENS/LSZH","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf",0.0678,0.35,1,10.856,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,0,500000,"500","CU 1 / C 2.4 kV Non Shielded Non Armored SOLONON XPL Jacketed"]
["2/0",175,"2/0",135,null,133100,{"$nulls":9},12,"35kV 420 Mil EPR 133% CU Tape",12,{"$nulls":8},1,1,6,1,3,11613,"CU","1/C","5KV","None","SIMpull PVC","500","95-50-54-99","78 x 54",2067,"N/A",1.3,470,505,3000,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-09ET SIMpull ","https://s3.amazonaws.com/swspec/MV/SPEC46102+CU+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf",0.0678,0.2,1,15.600000000000001,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1143,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
["3/0",200,"3/0",155,null,167800,{"$nulls":9},13,"2kV XLP  RHH / RHW-2 ",13,{"$nulls":8},1,1,7,1,3,11713,"CU","1/C","15KV 175","None","SIMpull PVC","500",95382899,"78 x 54",2201,"N/A",1.415,465,500,3500,"No","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC 11ET SIMpull ","https://s3.amazonaws.com/swspec/MV/SPEC46301+CU+1C+175NLEPR+tape+PVC-SIM+15KV+100.pdf",0.0678,0.2,1,16.98,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1258,500000,"500","CU 1 / C 15kV 175 Mil EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
["4/0",230,"4/0",180,null,211600,{"$nulls":4},"Times O.D.",{"$nulls":15},1,1,8,1,3,11813,"CU","1/C","15KV 220","None","SIMpull PVC","500","95-60-45-99","72 x 42",2317,"N/A",1.505,465,500,3000,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-13ET SIMpull PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",0.0678,0.2,1,18.06,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1348,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[250,255,250,205,null,250000,null,null,null,"Product",0,1,2,"Armored",{"$nulls":12},1,1,6,1,4,11614,"CU","1/C","5KV","None","CPE-PO","500","55-05-21-99","78 x 54",2137,"N/A",1.39,470,505,4000,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","CT1-09ET-C","https://s3.amazonaws.com/swspec/MV/SPEC46103+CU+1C+115NLEPR+tape+CPE+5KV+133.pdf",0.0678,0.5,1,16.68,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1143,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
["350",310,"350",250,null,350000,null,null,1,"600V RHH RHW USE (XLP) ",4,5,6,7,{"$nulls":12},1,1,8,1,4,11814,"CU","1/C","15KV 220","None","CPE-PO","500","55-05-08-99","78 x 42",2388,"N/A",1.567,465,500,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","CT1-13ET-C","https://s3.amazonaws.com/swspec/MV/SPEC46304+CU+1C+220NLEPR+tape+CPE+15KV+133.pdf",0.0678,0.5,1,18.804,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1348,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
["500",380,"500",310,null,500000,null,null,2,"600V XHHW ( XLP)",4,5,6,7,{"$nulls":12},1,1,6,1,6,11616,"CU","1/C","5KV","None","Solo PO","500","55-07-83-99","78 x 42",2137,"N/A",1.39,470,505,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","CT1-09ET-S","https://s3.amazonaws.com/swspec/MV/SPEC46104+CU+1C+115NLEPR+tape+LSZH+5KV+133.pdf",0.0678,0.35,1,16.68,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1200,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
["600",420,"600",340,null,600000,null,null,3,"600V THHN THWN",4,5,6,7,{"$nulls":12},1,1,8,1,6,11816,"CU","1/C","15KV 220","None","Solo PO","500","55-07-89-99","78 x 42",2355,"N/A",1.567,465,500,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","CT1-13ET-S","https://s3.amazonaws.com/swspec/MV/SPEC46305+CU+1C+220NLEPR+tape+LSZH+15KV+133.pdf",0.0678,0.35,1,18.804,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1410,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
["750",475,"750",385,null,750000,null,null,4,"1kV Non Shielded",8,"-","-","-",{"$nulls":12},1,1,9,1,3,11913,"CU","1/C","25KV 320 ","None","SIMpull PVC","500",64462399,0,2582,"N/A",1.715,465,500,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 75kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)",0,"http://media.industrial.southwire.com/spec/spec46000/SPEC46502+CU+1C+320NLEPR+tape+PVC-SIM+25KV+133.pdf",0.0678,0.2,1,20.580000000000002,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1.545,500000,"500","CU 1 / C 25kV 320 MIL EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
["1000",545,"1000",445,null,1000000,null,null,5,"2.4 kV Non Shielded",8,"-","-","-",{"$nulls":12},1,1,11,1,3,111113,"CU","1/C","35kV 345 ","None","SIMpull PVC","500",55588899,"78 x 54",2761,"N/A",1.813,465,500,2500,"No","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1 19ET SIMpull PVC JKT","https://s3.amazonaws.com/swspec/MV/SPEC46701+CU+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf",0.0678,0.2,1,21.756,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1593,500000,"500","CU 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacketed"]
[null,590,1250,485,null,1250000,null,null,6,"5kV 115 Mil EPR 133% CU Tape",7,12,"-","-",{"$nulls":12},1,1,12,1,3,111213,"CU","1/C","35KV 420","None","SIMpull PVC","500","89-00-68-99","84 x 62",3011,"N/A",1.965,465,500,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-21ET SIMpull PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46702+CU+1C+420NLEPR+tape+PVC-SIM+35KV+133.pdf",0.0678,0.2,1,23.580000000000002,"Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","N/A","1",500000,1745,500000,"500","CU 1 / C 35kV 420 Mil EPR 133% CU Tape Non Armored SIMpul- PVC Jacketed"]
[null,625,1500,520,null,1500000,null,null,7,"15kV 175 Mil EPR 100% CU Tape",7,12,"-","-",{"$nulls":12},1,2,6,1,2,12612,"CU","3/C WG","5KV","None","PVC","500",95839799,"104 x 57",7103,1,2.78,485,525,2000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT3-09ET PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46202+CU+3C+115NLEPR+tape+PVC+5KV+133.pdf",0.0678,0.35,3,19.459999999999997,"Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","N/A","3",500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Non Armored  PVC Jacketed"]
[{"$nulls":5},1620,null,null,8,"15kV 220 Mil EPR 133% CU Tape",7,12,"-","-",{"$nulls":12},1,2,8,1,2,12812,"CU","3/C WG","15KV 220","None","PVC","500",95833099,"96 x 63",8056,1,3.223,485,525,1000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT3-13ET PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46402+CU+3C+220NLEPR+tape+PVC+15KV+133.pdf",0.0678,0.35,3,22.561,"Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","N/A","3",500000,1348,1583690,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Non Armored PVC Jacketed"]
[{"$nulls":5},2580,null,null,9,"25kV 260 MIL EPR 100% CU Tape",7,12,"-","-",{"$nulls":12},1,2,5,1,2,12512,"CU","3/C WG","2.4 KV","None","PVC","500","60-03-87-99","92 x 55",6444,1,2.536,460,475,1750,"Yes","N/A",1000,"-10C (14F)","EFC CT3-09ENS PVC Jkt",0,0.0678,0.35,3,17.752,"Duct 310.79 @105 C","Conduit in Air 310.75 @105 C","N/A","3",500000,0,1500000,"500","CU 3 / C WG 2.4 kV Non Shielded Non Armored PVC Jacketed"]
[{"$nulls":8},10,"28kV 280 MIL EPR 100% CU Tape",7,12,"-","-",{"$nulls":12},1,2,2,3,2,12232,"CU","3/C WG","600 XHHW","AIA","PVC","500","38-06-18-99","92 x 55",6104,2,2.462,0,487,2000,"Yes","N/A","1000","-10C (14F)","AL01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45301+CU+3C+XLPE+XHHW+AIA+PVC+600V+W1CUGW.pdf",0.0719,0.35,3,17.234,0,"Free Air 90 C 310.3","N/A","3",500000,0,1566360,"500","CU 3 / C WG 600V AIA Armored PVC Jacketed"]
[{"$nulls":8},11,"35kV 345 MIL EPR 100% CU Tape",7,12,"-","-",{"$nulls":12},1,2,5,3,2,12532,"CU","3/C WG","2.4 KV","AIA","PVC","500","89-06-45-99","96 x 63",6556,1,2.687,530,485,2100,"Yes","N/A","1000","-10C (14F)","AL09ENS","https://s3.amazonaws.com/swspec/MV/SPEC46026+CU+3C+115EPR+none+AIA+PVC+2.4KV+100.pdf",0.0678,0.35,3,18.808999999999997,"Direct Burial 310.83 @ 90 C","Free Air 90 C 310.71","N/A","3",500000,0,1583690,"500","CU 3 / C WG 2.4 kV Non Shielded AIA Armored PVC Jacketed"]
[{"$nulls":8},12,"35kV 420 Mil EPR 133% CU Tape",7,12,"-","-",{"$nulls":12},1,2,6,3,2,12632,"CU","3/C WG","5 KV","AIA","PVC","500",55668899,"96 x 63",7262,1,2.957,590,600,1600,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ","1000","-10C (14F)","AL09ET","https://s3.amazonaws.com/swspec/MV/SPEC46254+CU+3C+115NLEPR+tape+AIA+PVC+5KV+133.pdf",0.0678,0.35,3,20.698999999999998,"Direct Burial 310.83 @ 105C","Free Air 105 C 310.71","N/A","3",500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
[{"$nulls":8},13,"2kV XLP  RHH / RHW-2 ",8,"-","-","-",{"$nulls":12},1,2,8,3,2,12832,"CU","3/C WG","15KV 220","AIA","PVC","500","40-91-69-99","108 x 71",8299,1,3.42,590,600,1600,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ","1000","-10C (14F)","AL13ET","https://s3.amazonaws.com/swspec/MV/SPEC46453+CU+3C+220NLEPR+tape+AIA+PVC+15KV+133.pdf",0.0678,0.35,3,23.939999999999998,"Direct Burial 310.83","Free Air 105 C 310.71","N/A","3",500000,1348,1583690,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
[{"$nulls":26},1,3,2,4,2,13242,"CU","4/C WG","600 XHHW","Armor-X","PVC","500",89053699,"96 x 55",7721,"1 x #2",2.82,0,344,1500,"YES","N/A",1000,"-40C (-40F)","HLX01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45352+CU+4C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf",0.0719,0.35,4,19.74,0,"4/C @ 90 C 310.16","N/A","4",500000,0,2066360,"500"," CU 4 / C WG Armor-X (CCW) Armored PVC Jacketed"]
[{"$nulls":26},1,2,2,4,2,12242,"CU","3/C WG","600 XHHW","Armor-X","PVC","500",89052299,"84 x 54",6001,"3 x #6",2.58,0,430,1500,"YES","N/A",1000,"-40C (-40F)","HLX01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45351+CU+3C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf",0.0719,0.35,3,18.060000000000002,0,"90 C 310.16","N/A","3",500000,0,1578720,"500","CU 3 / C WG 600V Armor-X (CCW) Armored PVC Jacketed"]
[{"$nulls":10},"0 cable(s) 500 CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed",{"$nulls":15},1,2,5,4,2,12542,"CU","3/C WG","2.4 KV","Armor-X","PVC","500",89062199,"96 x 55",6571,"3x4",2.82,530,485,1500,"YES","N/A",1000,"-40C (-40F)","XAL07ENS","https://s3.amazonaws.com/swspec/MV/SPEC46027+CU+3C+90EPR+none+ARMOR-X+PVC+2.4KV+100.pdf",0.0678,0.35,3,19.74,"Direct Burial 310.83 @ 90C","Free Air 105 C 310.71 @ 90C","N/A","3",500000,0,1500000,"500","CU 3 / C WG 2.4 kV Non Shielded Armor-X (CCW) Armored PVC Jacketed"]
[{"$nulls":9},"Cond","500",{"$nulls":15},1,2,6,4,2,12642,"CU","3/C WG","5KV","Armor-X","PVC","500",89064399,"96 x 55",7363,1,3.13,570,545,1300,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","HLX09ET","https://s3.amazonaws.com/swspec/MV/SPEC46255+CU+3C+115NLEPR+tape+ARMOR-X+PVC+5KV+133.pdf",0.0678,0.35,3,21.91,"Direct Burial 310.83 @ 105C","Free Air 105 C 310.71@ 105C","N/A","3",500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
["Sides updated 5-24-13",{"$nulls":9},"CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed",{"$nulls":15},1,2,8,4,2,12842,"CU","3/C WG","15KV 220","Armor-X","PVC","500",89066999,"108 x 71  ",8674,1,3.71,590,600,1300,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","HLX13ET","https://s3.amazonaws.com/swspec/MV/SPEC46454+CU+3C+220NLEPR+tape+ARMOR-X+PVC+15KV+133.pdf",0.0678,0.35,3,25.97,"Direct Burial 310.83","Free Air 105 C 310.71","N/A","3",500000,1348,1500000,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
[{"$nulls":9},"Qty",0,{"$nulls":15},1,2,4,5,2,12452,"CU","3/C WG","1KV","Tech 90","PVC","500",56196199,"84 x 54",6802,3,2.777,0,0,1500,0,"N/A","1000","-40 C (-40 F)","3/C 1kV Tech 90","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheetT90",0.0678,0.35,3,41.655,"Amps",0,"N/A","3",500000,0,1552620,"500","CU 3 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[{"$nulls":9},"Gnd",0,{"$nulls":15},1,3,4,5,2,13452,"CU","4/C WG","1KV","Tech 90","PVC","500",56196299,"96 x 55",8602,3,3.024,0,0,1000,0,"N/A","1000","-40C (-40F)","4/C 1kV Tech 90","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet329",0.0678,0.35,4,45.36,"Amps",0,"N/A","4",500000,0,2052620,"500","CU 4 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[{"$nulls":9},"Qty",0,"",{"$nulls":14},2,1,2,1,1,21211,"AL","1 / C","600V XHHW ( XLP)","None","None","500",56038099,"66 x 42",567,"N/A",0.869,310,350,4500,"Yes","N/A","1000","- 40C (-40F)","AL XHHW/CT","http://media.industrial.southwire.com/spec/spec45000/SPEC45007+AL+1C+XLPE+XHHW+none+600V+.pdf",0.047,0.35,1,3.476,"In Duct NEC 310.15 75 C","In Duct NEC 310.15 90 C","N/A","1",500000,0,500000,"500","AL 1 / C 600V XHHW ( XLP) Non Armored Non Jacketed"]
[{"$nulls":10},false,"SIMpull CU THHN",{"$nulls":14},2,1,6,1,3,21613,"AL","1 / C","5kV 115 Mil EPR 133% CU Tape","None","SIMpull PVC","500",56014799,"72 x 42",961,"N/A",1.25,370,400,3000,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-09ET","https ://s3.amazonaws.com/swspec/MV/SPEC46110+AL+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf",0.0443,0.2,1,15,"Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","N/A","1",500000,1035,500000,"500","AL 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[{"$nulls":26},2,1,8,1,3,21813,"AL","1 / C","15kV 220 Mil EPR 133% CU Tape","None","SIMpull PVC","500",56011799,"72 x 42",1259,"N/A",1.508,370,400,3000,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-13ET","https://s3.amazonaws.com/swspec/MV/SPEC46311+AL+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",0.0443,0.2,1,18.096,"Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","N/A","1",500000,1290,500000,"500","AL 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[{"$nulls":9},0,{"$nulls":16},2,1,11,1,3,211113,"AL","1 / C","35kV 345 MIL EPR 100% CU Tape","None","SIMpull PVC","500",58089599,"78 x 54",1622,"N/A",1.765,370,400,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-19ET","https://s3.amazonaws.com/swspec/MV/SPEC46709+AL+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf",0.0443,0.2,1,21.18,"Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","N/A","1",500000,0,500000,"500","AL 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
[{"$nulls":10}," and "," and ",{"$nulls":14},1,2,8,1,4,12814,"CU","3/C WG","15kV 220 Mil EPR 133% CU Tape","None","CPE-PO","500",56123299,"96 x 63",8162,1,3.48,485,525,1000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","EFC CT3-13ET CPE Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46403+CU+3C+220NLEPR+tape+CPE+15KV+133.pdf",0.0678,0.5,3,24.36,"Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","N/A","3",500000,1348,1583690,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Non Armored CPE Jacketed"]
[{"$nulls":10},", "," and ",{"$nulls":14},1,2,6,1,4,12614,"CU","3/C WG","5kV 115 Mil EPR 133% CU Tape","None","CPE-PO","500",56123099,"96 x 62.5",7089,1,2.767,485,525,2000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","EFC CT3-09ET CPE Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46203+CU+3C+115NLEPR+tape+CPE+5KV+133.pdf",0.0678,0.5,3,19.369,"Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","N/A","3",500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Non Armored CPE Jacketed"]
[{"$nulls":26},1,2,13,1,4,121314,"CU","3/C WG","2kV XLP  RHH / RHW-2 ","None","CPE-PO","500",56601699,"78 x 54",6187,2,2.396,430,"N/A",1500,"Yes","N / A",1000,"-20C (-4F)","3/C 2kV RHH/RHW CPE Jacketed TC","http://media.industrial.southwire.com/spec/spec45000/SPEC45451+CU+3C+XLPE+RHW+PVC+2000V+W3CUGW+VFD.pdf",0.0678,0.5,3,16.772,"Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","N/A","3",500000,0,1583690,"500","CU 3 / C WG 2kV XLP RHH/ RHW-2  Non Armored CPE Jacketed"]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
["Raymond",{"$nulls":51}," "]
[null,null,"CU or AL","CU",{"$nulls":48}," "]
[null,null,"Conductor count","1 / C",{"$nulls":48}," "]
[null,null,"Voltage / Ins  level / shield","600V SIMpull XHHW ( XLP)",{"$nulls":48}," "]
[null,null,"Armor","None",{"$nulls":48}," "]
[null,null,"Jacket","None",{"$nulls":48}," "]
[null,null,"Max Sidewall pressure ",1000,{"$nulls":48}," "]
[null,null,"High Potential testing","N/A",{"$nulls":48}," "]
[null,null,"Min Installation Temp","- 40C (-40F)",{"$nulls":48}," "]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/spec45000/SPEC45001+CU+1C+XLPE-SIM+XHHW+none+600V+.pdf",{"$nulls":48}," "]
[null,null,"Product #","XHHW/CT",{"$nulls":48}," "]
[null,null,"Spec #",45001,{"$nulls":48}," "]
["1/C 600V SIMpull XHHW-2 CT RATED",{"$nulls":10},"CU 1 / C 600V SIMpull XHHW ( XLP)",{"$nulls":40}," "]
[{"$nulls":6},"Ampacity # 1","Ampacity #2",{"$nulls":44}," "]
[{"$nulls":52}," "]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 90C NEC 310.16","In Cable Tray Free Air NEC 392.11 @ 90 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions",{"$nulls":37}," "]
[{"$nulls":52}," "]
["14 Str",{"$nulls":51}," "]
["12 Str",{"$nulls":51}," "]
["10 Str",{"$nulls":51}," "]
["8",{"$nulls":51}," "]
[6,{"$nulls":51}," "]
[4,{"$nulls":51}," "]
[2,{"$nulls":51}," "]
[1,{"$nulls":51}," "]
["1/0",55344699,"60 X 28",369,"N/A",0.475,170,260,15000,"Yes",null,1.9,105600,null,105600,{"$nulls":37}," "]
["2/0",60051099,"50 x 38",458,"N/A",0.518,195,300,10000,"Yes",null,2.072,133100,null,133100,{"$nulls":37}," "]
["3/0",55705899,"60 x 28",572,"N/A",0.569,225,350,10000,"Yes",null,2.276,167800,null,167800,{"$nulls":37}," "]
["4/0",42971299,"50 x 38",713,"N/A",0.623,260,405,7000,"Yes",null,2.492,211600,null,211600,{"$nulls":37}," "]
[250,55702599,"84 x 42",844,"N/A",0.691,290,455,10000,"Yes",null,2.764,250000,null,250000,{"$nulls":37}," "]
["350",55087199,"72 x 42",1166,"N/A",0.794,350,570,7000,"Yes",null,3.176,350000,null,350000,{"$nulls":37}," "]
["500",55701799,"66 x 42",1645,"N/A",0.923,430,700,4500,"Yes",null,3.692,500000,null,500000,{"$nulls":37}," "]
["600",60457999,"64 x 42",1982,"N/A",1.029,475,780,4000,"Yes",null,5.145,600000,null,600000,{"$nulls":37}," "]
["750",55102899,"84 x 42",2458,"N/A",1.131,535,885,3000,"Yes",null,5.655,750000,null,750000,{"$nulls":37}," "]
["1000","55-74-88-99","64 x 42",3250,"N/A",1.28,615,1055,2500,"Yes",null,6.4,1000000,null,1000000,{"$nulls":37}," "]
[1250,{"$nulls":51}," "]
[1500,{"$nulls":51}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
[{"$nulls":52}," "]
["Hooper",{"$nulls":51}," "]
[null,null,"CU or AL","CU",{"$nulls":27},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","600V RHH RHW USE (XLP) "]
[null,null,"Armor","None"]
[null,null,"Jacket","None"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","- 40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/spec45000/SPEC45003+CU+1C+XLPE+RHW+none+600V+.pdf"]
[null,null,"Product #","RHH or RHW-2 / CT"]
[null,null,"Spec # ",45003]
["1/C 600V RHH/RHW-2 CT RATED",{"$nulls":10},"CU 1 / C 600V RHH RHW USE (XLP) Non Armored Non Jacketed"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 90C NEC 310.16","In Cable Tray Free Air NEC 392.11","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,"95-58-72-99","48 x 32",245,"N/A",0.401,null,null,null,"No",null,1.604,66360,null,66360]
[1]
["1/0",89010599,"60 x 28",390,"N/A",0.525,170,260,15000,"Yes",null,2.1,105600,null,105600]
["2/0",89010699,"72 x 42",481,"N/A",0.568,195,300,10000,"Yes",null,2.272,133100,null,133100]
["3/0",89063199,"60 x 28",597,"N/A",0.619,225,350,10000,"Yes",null,2.476,167800,null,167800]
["4/0",89010799,"72 x 42",741,"N/A",0.675,260,405,10000,"Yes",null,2.7,211600,null,211600]
[250,89063299,"84 x 42",880,"N/A",0.751,290,455,10000,"Yes",null,3.004,250000,null,250000]
["350",89010899,"72 x 42",1207,"N/A",0.854,350,570,7000,"Yes",null,3.416,350000,null,350000]
["500",89010999,"66 x 42",1693,"N/A",0.983,430,700,4500,"Yes",null,3.932,500000,null,500000]
["600",{"$nulls":13},600000]
["750",89063399,"84 x 42",2516,"N/A",1.191,535,885,3000,"Yes",null,5.955,750000,null,750000]
["1000",89011099,"78 x 54",3315,"N/A",1.34,615,1055,2500,"Yes",null,6.7,1000000,null,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","600V XHHW ( XLP)"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/spec45000/SPEC45002+CU+1C+XLPE+XHHW+PVC+600V+.pdf"]
[null,null,"Product #","XHHW/PVC CT"]
[null,null,"Spec #",45002]
["1/C 600V XLP/PVC CT RATED",{"$nulls":10},"CU 1 / C 600V XHHW ( XLP) Non Armored PVC Jacketed"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 90 C NEC 310.16","In Cable Tray Free Air NEC 318.11 @ 90 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2]
[1]
["1/0",89041999,"60 x 32",412,"N/A",0.565,170,260,10000,"Yes",null,2.26,105600,null,105600]
["2/0",89018199,"58 x 35",505,"N/A",0.608,195,300,10000,"Yes",null,2.432,133100,null,133100]
["3/0",89042199,"66 x 33",623,"N/A",0.659,225,350,10000,"Yes",null,2.636,167800,null,167800]
["4/0",89018099,"66 x 33",769,"N/A",0.715,260,405,8000,"Yes",null,2.86,211600,null,211600]
[250,89002399,"72 x 42",934,"N/A",0.821,290,455,8000,"Yes",null,3.284,250000,null,250000]
["350",89017999,"72 x 42",1268,"N/A",0.924,350,570,8000,"Yes",null,3.696,350000,null,350000]
["500",89002299,"66 x 42",1763,"N/A",1.053,430,700,4000,"Yes",null,5.265,500000,null,500000]
["600",{"$nulls":13},600000]
["750",89002499,"72 x 42",2602,"N/A",1.261,535,885,3000,"Yes",null,6.305,750000,null,750000]
["1000",89043099,"66 x 42",3411,"N/A",1.41,615,1055,2000,"Yes",null,7.05,1000000,null,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V THHN THWN"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC THHN"]
[null,null,"Spec #",45251]
["600v, 3c, THHN/PVC, WG, PVC Jacket, Type TC Power",{"$nulls":10},"CU 3 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
[]
[]
[" 3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str","60-68-06-99",null,93,"14 green",0.35,15,25,null,"Yes",null,1.4,4110,null,16440]
["12 Str","60-67-23-99",null,126,"12 green",0.392,20,30,null,"Yes",null,1.568,6530,null,26120]
["10 Str","60-55-43-99",null,198,"10 green",0.473,30,40,null,"Yes",null,1.892,10380,null,41520]
["8",44339099,"45 x 35",295,"10 bare",0.625,50,55,6000,"Yes",null,2.5,16510,null,59910]
[6,44340899,"50 x 34",435,"8 bare",0.71,65,75,6000,"Yes",null,2.84,26240,null,78720]
[4,44341699,"66 x 36",606,"8 bare",0.795,85,95,6000,"Yes",null,3.18,41740,null,125220]
[2,44342499,"72 x 44",942,"6 bare",0.958,115,130,6000,"Yes",null,3.832,66360,null,225320]
[1,"44-34-32-99","78 x 42",1195,"6 bare",1.1,130,150,6000,"Yes",null,5.5,83690,null,277310]
["1/0",44344099,"78 x 42",1445,"6 bare",1.184,150,170,5000,"Yes",null,5.92,105600,null,343040]
["2/0",44345799,"78  x54",1734,"6 bare",1.281,175,195,5000,"Yes",null,6.404999999999999,133100,null,425540]
["3/0",44346599,"72 x 42",2163,"4 bare",1.391,200,225,3000,"Yes",null,6.955,167800,null,545140]
["4/0",44347399,"78 x 42",2617,"4 bare",1.508,230,260,3000,"Yes",null,7.54,211600,null,676540]
[250,44348199,"72 x 42",3070,"4 bare",1.659,255,290,2000,"Yes",null,8.295,250000,null,791740]
["350",44350799,"84 x 54",4276,"3 bare",1.942,310,350,2000,"Yes",null,9.709999999999999,350000,null,1102620]
["500",44352399,"92 x 55",5906,"2 bare",2.22,380,430,2000,"Yes",null,13.32,500000,null,1566360]
["600",{"$nulls":10},0,600000]
["750",60209499,"84 x 54",8609,"1 bare",2.652,475,535,1000,"Yes",null,15.912,750000,null,2333690]
["1000"]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","4 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V THHN THWN"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC THHN"]
[null,null,"Spec #",45257]
["600v, 4c, THHN/PVC, WG, PVC Jacket, Type TC Power",{"$nulls":10},"CU 4 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
[]
[]
[" 4/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str","60-68-14-99",null,109,"14 green",0.381,15,25,null,"Yes",null,1.524,4110,null,20550]
["12 Str","60-67-98-99",null,154,"12 green",0.426,20,30,null,"Yes",null,1.704,6530,null,32650]
["10 Str","60-68-63-99",null,250,"10 green",0.549,30,40,null,"Yes",null,2.196,10380,null,51900]
["8",55769499,"60 x 28",369,"10 bare",0.685,50,55,9000,"Yes",null,2.74,16510,null,76420]
[6,55343899,"66 x 42",549,"8 bare",0.78,65,75,9000,"Yes",null,3.12,26240,null,104960]
[4,60198999,"68 x 44",808,"8 bare",0.914,85,95,6000,"Yes",null,3.656,41740,null,166960]
[2,60199799,"78 x 54",1197,"6 bare",1.052,115,130,7000,"Yes",null,5.26,66360,null,291680]
[1,"60-20-03-99","78 x 54",1532,"6 bare",1.21,130,150,6000,"Yes",null,6.05,83690,null,361000]
["1/0",55456899,"78 x 54",1838,"6 bare",1.304,150,170,4500,"Yes",null,6.5200000000000005,105600,null,448640]
["2/0",55672099,"78 x 42",2238,"6 bare",1.413,175,195,3500,"Yes",null,7.065,133100,null,558640]
["3/0",60202999,"78 x 42",2782,"4 bare",1.536,200,225,3500,"Yes",null,7.68,167800,null,712940]
["4/0",44474599,"78 x 54",3477,"4 bare",1.726,230,260,2500,"Yes",null,8.629999999999999,211600,null,888140]
[250,60204599,"78 x 54",4095,"4 bare",1.895,255,290,2000,"Yes",null,9.475,250000,null,1041740]
["350",60206099,"78 x 54",5530,"3 bare",2.144,310,350,1500,"Yes",null,12.864,350000,null,1441740]
["500",55251399,"92 x 55",7652,"2 bare",2.455,380,430,1500,"Yes",null,14.73,500000,null,2066360]
["600",60481999,{"$nulls":7},"Yes",null,0,600000]
["750","60-48-27-99","84 x 62",11365,"1 bare",2.998,475,535,800,"Yes",null,17.988,750000,null,3083690]
["1000"]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V XHHW / XLP"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45252+CU+3C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC XHHW"]
[null,null,"Spec #",45252]
["600V, 3/C, XLP (XHHW), W/G, PVC JACKET, TYPE TC Power",{"$nulls":10},"CU 3 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
[]
[]
[" 3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str","95-58-31-99",null,106,"14 green",0.403,15,25,null,"Yes",null,1.612,4110,null,16440]
["12 Str","95-59-30-99",null,147,"12 green",0.445,20,30,null,"Yes",null,1.78,6530,null,26120]
["10 Str","95-59-55-99",null,205,"10 green",0.502,30,40,null,"Yes",null,2.008,10380,null,41520]
["8"," 48-05-90-99","58 x 37",330,"10 bare",0.681,50,55,6000,"Yes",null,2.724,16510,null,59910]
[6," 48-06-08-99","58 x 37",468,"8 bare",0.766,65,75,6000,"Yes",null,3.064,26240,null,78720]
[4," 48-06-16-99","66 x 36",606,"8 bare",0.797,85,95,6000,"Yes",null,3.188,41740,null,125220]
[2," 48-06-24-99","72 x 42",954,"6 bare",0.96,115,130,6000,"Yes",null,3.84,66360,null,225320]
[1," 48-06-32-99","78 x 42",1173,"6 bare",1.1,130,150,6000,"Yes",null,5.5,83690,null,277310]
["1/0"," 48-06-40-99","78 x 42",1421,"6 bare",1.186,150,170,5000,"Yes",null,5.93,105600,null,343040]
["2/0"," 48-06-57-99","78 x 54",1704,"6 bare",1.279,175,195,5000,"Yes",null,6.395,133100,null,425540]
["3/0"," 48-06-65-99","72 x 42",2134,"4 bare",1.385,200,225,3000,"Yes",null,6.925,167800,null,545140]
["4/0"," 48-06-73-99","78 x 42",2580,"4 bare",1.506,230,260,3000,"Yes",null,7.53,211600,null,676540]
[250," 48-06-81-99","72 x 42",3021,"4 bare",1.653,255,290,2000,"Yes",null,8.265,250000,null,791740]
["350"," 48-07-07-99","84 x 54",4219,"3 bare",1.935,310,350,2000,"Yes",null,9.675,350000,null,1102620]
["500"," 48-07-23-99","92 x 55",5755,"2 bare",2.214,380,430,2000,"Yes",null,13.283999999999999,500000,null,1566360]
["600","89-03-88-99",{"$nulls":7},"Yes",null,0,600000]
["750","* 55-44-10-99  ","96 x 63",8543,"1 bare",2.663,475,535,1500,"Yes",null,15.977999999999998,750000,null,2333690]
["1000"]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","4 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V XHHW / XLP"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45258+CU+4C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC XHHW"]
[null,null,"Spec #",45258]
["600V, 4/C, XLP (XHHW), W/G, PVC JACKET,  TYPE TC Power",{"$nulls":10},"CU 4 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
[]
[]
[" 4/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str","95-58-23-99",null,125,"14 green",0.44,15,25,null,"Yes",null,1.76,4110,null,20550]
["12 Str","95-59-48-99",null,171,"12 green",0.487,20,30,null,"Yes",null,1.948,6530,null,32650]
["10 Str","95-59-63-99",null,260,"10 green",0.581,30,40,null,"Yes",null,2.324,10380,null,51900]
["8",55700999,"58 x 37",404,"10 bare",0.747,50,55,6000,"Yes",null,2.988,16510,null,76420]
[6,56010299,"58 x 37",613,"8 bare",0.882,65,75,6000,"Yes",null,3.528,26240,null,104960]
[4,55699399,"68 x 44",802,"8 bare",0.917,85,95,6000,"Yes",null,3.668,41740,null,166960]
[2,55430399,"78 x 54",1191,"6 bare",1.054,115,130,8000,"Yes",null,5.2700000000000005,66360,null,291680]
[1,60201199,"78 x 54",1503,"6 bare",1.21,130,150,6500,"Yes",null,6.05,83690,null,361000]
["1/0",55443699,"78 x 54",1806,"6 bare",1.307,150,170,5000,"Yes",null,6.535,105600,null,448640]
["2/0",55698599,"78 x 54",2199,"6 bare",1.411,175,195,4500,"Yes",null,7.055,133100,null,558640]
["3/0",60203799,"78 x 54",2744,"4 bare",1.529,200,225,3500,"Yes",null,7.645,167800,null,712940]
["4/0",55444499,"92 x 55",3427,"4 bare",1.724,230,260,3500,"Yes",null,8.62,211600,null,888140]
[250,60205299,"92 x 55",4030,"4 bare",1.888,255,290,3000,"Yes",null,9.44,250000,null,1041740]
["350",60207899,"92 x 55",5453,"3 bare",2.137,310,350,2000,"Yes",null,12.822,350000,null,1452620]
["500",55446999,"92 x 55",7562,"2 bare",2.448,380,430,1500,"Yes",null,14.687999999999999,500000,null,2066360]
["600"]
["750"]
["1000"]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V XHHW / XLP"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","- 40C (-40F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45255+CU+3C+EPR+XHHW+CPE+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC XHHW CPE"]
[null,null,"Spec #",45255]
["600V, 3/C, FR XLP (XHHW), W/G, CPE JACKET",{"$nulls":10},"CU 3 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[]
[]
[" 3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",null,null,104,"14 Green",0.403,15,25,null,"Yes",null,1.612,4110,null,16440]
["12 Str",null,null,145,"12 Green",0.445,20,30,null,"Yes",null,1.78,6530,null,26120]
["10 Str",null,null,204,"10 Green",0.502,30,40,null,"Yes",null,2.008,10380,null,41520]
["8","89-06-70-99","58 x 37",327,"10 bare",0.681,50,55,6000,"Yes",null,2.724,16510,null,59910]
[6,"89-06-71-99","58 x 37",465,"8 bare",0.766,65,75,6000,"Yes",null,3.064,26240,null,78720]
[4,"89-06-72-99","66 x 36",610,"8 bare",0.797,85,95,6000,"Yes",null,3.188,41740,null,125220]
[2,"89-06-73-99","72 x 42",958,"6 bare",0.96,115,130,6000,"Yes",null,3.84,66360,null,225320]
[1,89070199,"78 x 42",1169,"6 bare",1.097,130,150,6000,"Yes",null,5.484999999999999,83690,null,277310]
["1/0",89070299,"72 x 42",1426,"6 bare",1.182,150,170,5000,"Yes",null,5.91,105600,null,343040]
["2/0",89070399,"78 x 54",1711,"6 bare",1.277,175,195,5000,"Yes",null,6.385,133100,null,425540]
["3/0",89070499,"72 x 44",2144,"4 bare",1.385,200,225,3000,"Yes",null,6.925,167800,null,545140]
["4/0",89070599,"78 x 42",2591,"4 bare",1.506,230,260,3000,"Yes",null,7.53,211600,null,676540]
[250,89070699,"72 x 44",3036,"4 bare",1.653,255,290,2000,"Yes",null,8.265,250000,null,791740]
["350",89070899,"78 x 54",4231,"3 bare",1.935,310,350,2000,"Yes",null,9.675,350000,null,1102620]
["500",89071099,"78 x 54",5853,"2 bare",2.214,380,430,1500,"Yes",null,13.283999999999999,500000,null,1566360]
["600"]
["750",89071299,"96 x 63",8568,"1 bare",2.663,475,535,1500,"Yes",null,15.977999999999998,750000,null,2333690]
["1000"]
[1250]
[1500]
[]
[]
[]
["hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","4 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V XHHW / XLP"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","- 40C (-40F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45262+CU+4C+EPR+XHHW+CPE+600V+W1CUGW.pdf"]
[null,null,"Product #","Type TC XHHW/CPE"]
[null,null,"Spec #",45262]
["600V, 4/C, FR XLP (XHHW), W/G, CPE JACKET",{"$nulls":10},"CU 4 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[]
[]
[" 4/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","75 C 310.16","90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",null,null,123,"14 Green",0.44,15,25,null,"Yes",null,1.76,4110,null,20550]
["12 Str",null,null,170,"12 Green",0.487,20,30,null,"Yes",null,1.948,6530,null,32650]
["10 Str",null,null,257,"10 Green",0.581,30,40,null,"Yes",null,2.324,10380,null,51900]
["8","55-03-79-99","58 x 37",401,"10 bare",0.747,50,55,6000,"Yes",null,2.988,16510,null,76420]
[6,"55-03-80-99","58 x 37",607,"8 bare",0.882,65,75,6000,"Yes",null,3.528,26240,null,104960]
[4,"55-03-81-99","68 x 44",807,"8 bare",0.917,85,95,6000,"Yes",null,3.668,41740,null,166960]
[2,"55-03-82-99",null,1197,"6 bare",1.054,115,130,null,"Yes",null,5.2700000000000005,66360,null,291680]
[1,"55-03-83-99","78 x 54",1511,"6 bare",1.208,130,150,6500,"Yes",null,6.04,83690,null,361000]
["1/0","55-03-85-99","78 x 54",1814,"6 bare",1.302,150,170,5000,"Yes",null,6.51,105600,null,448640]
["2/0","55-03-86-99",null,2210,"6 bare",1.408,175,195,null,"Yes",null,7.039999999999999,133100,null,558640]
["3/0","55-03-87-99","78 x 54",2759,"4 bare",1.529,200,225,3500,"Yes",null,7.645,167800,null,712940]
["4/0","55-03-88-99","92 x 55",3439,"4 bare",1.724,230,260,3500,"Yes",null,8.62,211600,null,888140]
[250,"55-03-89-99","92 x 55",4046,"4 bare",1.888,255,290,3000,"Yes",null,9.44,250000,null,1041740]
["350","55-03-90-99","92 x 55",5474,"3 bare",2.137,310,350,2000,"Yes",null,12.822,350000,null,1452620]
["500","55-03-91-99","92 x 55",7586,"2 bare",2.448,380,430,1500,"Yes",null,14.687999999999999,500000,null,2066360]
["600"]
["750"]
["1000"]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","2.4 kV Non Shielded"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf"]
[null,null,"Product #","EFC 09ENS/SIMpull PVC"]
[null,null,"Spec #",46002]
["Catalog Spec:  09ENS/PVC (CT RATED) SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 2.4 kV Non Shielded Non Armored SIMpull-PVC Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,253,"N/A",0.645,85,92,null,"No",null,5.16,26240,null,26240]
[4,null,null,321,"N/A",0.692,110,120,null,"No",null,5.536,41740,null,41740]
[2,"60-74-57-99",null,422,"N/A",0.75,145,155,null,"No",null,6,66360,null,66360]
[1,"60-74-65-99",null,489,"N/A",0.789,170,180,null,"No",null,6.312,83690,null,83690]
["1/0","60-72-26-99","64 x 54",574,"N/A",0.829,195,210,10000,"Yes ",null,6.632,105600,null,105600]
["2/0","60-72-34-99","78 x 42",676,"N/A",0.871,220,235,10000,"Yes ",null,6.968,133100,null,133100]
["3/0","60-72-42-99","78 x 54",834,"N/A",0.954,250,270,10000,"Yes ",null,7.632,167800,null,167800]
["4/0","60-72-59-99","78 x 54",995,"N/A",1.01,290,310,8000,"Yes ",null,8.08,211600,null,211600]
[250,"60-72-67-99","78 x 54",1199,"N/A",1.127,320,345,8000,"Yes ",null,9.016,250000,null,250000]
["350","60-72-83-99","78 x 54",1560,"N/A",1.229,385,415,6000,"Yes ",null,9.832,350000,null,350000]
["500","60-73-09-99","78 x 54",2088,"N/A",1.357,470,505,4000,"Yes ",null,10.856,500000,null,500000]
["600"]
["750","60-71-19-99","78 x 54",3044,"N/A",1.608,585,630,3000,"Yes ",null,12.864,750000,null,750000]
["1000","60-73-25-99","78 x 42",3897,"N/A",1.756,670,720,2000,"Yes ",null,14.048,1000000,null,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","2.4 kV Non Shielded"]
[null,null,"Armor","None"]
[null,null,"Jacket","SOLONON XLP"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf"]
[null,null,"Product #","EFC 09ENS/LSZH"]
[null,null,"Spec #",46003]
["Catalog Spec: 09ENS/LS (CT Rated)",{"$nulls":5},"SOLONON XLPJACKET",{"$nulls":4},"CU 1 / C 2.4 kV Non Shielded Non Armored SOLONON XPL Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,258,"N/A",0.645,85,92,null,"No",null,5.16,26240,null,26240]
[4,null,null,326,"N/A",0.692,110,120,null,"No",null,5.536,41740,null,41740]
[2,95854699,"66 x 42",427,"N/A",0.75,145,155,10000,"No",null,6,66360,null,66360]
[1,95855399,"64 x 54",495,"N/A",0.789,170,180,10000,"No",null,6.312,83690,null,83690]
["1/0",61109599,"58 x 37",598,"N/A",0.85,195,210,5000,"YES",null,6.8,105600,null,105600]
["2/0",61110399,"68 x 44",683,"N/A",0.871,220,235,5000,"YES",null,6.968,133100,null,133100]
["3/0",61111199,"66 x 36",842,"N/A",0.953,250,270,5000,"YES",null,7.624,167800,null,167800]
["4/0",61112999,"66 x 36",1003,"N/A",1.009,290,310,4000,"YES",null,8.072,211600,null,211600]
[250,61113799,"66 x 42",1210,"N/A",1.127,320,345,4000,"YES",null,9.016,250000,null,250000]
["350",61115299,"78 x 54",1572,"N/A",1.229,385,415,6000,"YES",null,9.832,350000,null,350000]
["500",61117899,"78 x 54",2101,"N/A",1.357,470,505,4000,"YES",null,10.856,500000,null,500000]
["600",null,null,null,"N/A"]
["750",61119499,"78 x 54",3062,"N/A",1.608,585,630,3000,"YES",null,12.864,750000,null,750000]
["1000",61120299,"72 x 42",3908,"N/A",1.756,670,720,2000,"YES",null,14.048,1000000,null,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46102+CU+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf"]
[null,null,"Product #","EFC CT1-09ET SIMpull "]
[null,null,"Spec #",46102]
["CATALOG SPEC: EFC CT1- 09ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,282,"N/A",0.656,85,92,null,"No",0.52,7.872,26240,530,26240]
[4,null,null,351,"N/A",0.701,110,120,null,"No",0.568,8.411999999999999,41740,578,578]
[2,"95-46-36-99","64 x 54",455,"N/A",0.759,145,155,10000,"No",0.623,9.108,66360,633,66360]
[1,"95-46-44-99",null,525,"N/A",0.799,170,180,10000,"No",0.663,9.588000000000001,83690,673,83690]
["1/0",95500599,"78 x 42",641,"N/A",0.87,195,210,10000,"YES",0.703,10.44,105600,713,105600]
["2/0","95-50-13-99","84 x 54",745,"N/A",0.91,220,235,10000,"YES",0.743,10.92,133100,753,133100]
["3/0","95-50-21-99","84 x 54",877,"N/A",0.96,250,270,8000,"YES",0.793,11.52,167800,803,167800]
["4/0","95-50-88-99","84 x 54",1036,"N/A",1.015,290,310,8000,"YES",0.848,12.18,211600,858,211600]
[250,"95-50-39-99","78 x 54",1181,"N/A",1.07,320,345,7000,"YES",0.905,12.84,250000,915,250000]
["350","95-50-47-99","78 x 42",1543,"N/A",1.175,385,415,4000,"YES",1.008,14.100000000000001,350000,1018,350000]
["500","95-50-54-99","78 x 54",2067,"N/A",1.3,470,505,3000,"YES",1.133,15.600000000000001,500000,1143,500000]
["600"]
["750","95-50-96-99","78 x 54",2932,"N/A",1.487,585,630,2500,"YES",1.32,17.844,750000,1330,750000]
["1000","95-50-70-99","78 x 42",3771,"N/A",1.632,670,720,2000,"YES",1.465,19.584,1000000,1475,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","15kV 175 Mil EPR 100% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46301+CU+1C+175NLEPR+tape+PVC-SIM+15KV+100.pdf"]
[null,null,"Product #","EFC 11ET SIMpull "]
[null,null,"Spec # ",46301]
["CATALOG SPEC:   EFC 11- ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 15kV 175 Mil EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield ","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,95372999,null,565,"N/A",0.905,155,165,null,"No",0.738,10.86,66360,748,66360]
[1,60522099,"66 x 36",640,"N/A",0.945,175,185,5000,"No",0.778,11.34,83690,788,83690]
["1/0",95375299,"68 x 44",731,"N/A",0.985,200,215,5000,"No",0.818,11.82,105600,828,105600]
["2/0",95376099,null,839,"N/A",1.025,230,245,null,"No",0.858,12.299999999999999,133100,868,133100]
["3/0",60523899,"64 x 54",976,"N/A",1.075,260,275,5000,"No",0.908,12.899999999999999,167800,918,167800]
["4/0",95377899,null,1144,"N/A",1.13,295,315,null,"No",0.963,13.559999999999999,211600,973,211600]
[250,95378699,"78 x 42",1294,"N/A",1.185,325,345,5000,"No",1.018,14.22,250000,1028,250000]
["350",95380299,null,1666,"N/A",1.29,390,415,null,"No",1.123,15.48,350000,1133,350000]
["500",95382899,"78 x 54",2201,"N/A",1.415,465,500,3500,"No",1.248,16.98,500000,1258,500000]
["600"]
["750",95384499,"78 x 54",3084,"N/A",1.602,565,610,2500,"No",1.435,19.224,750000,1445,750000]
["1000",60527999,"78 x 54",4039,"N/A",1.81,640,690,2000,"No",1.58,21.72,1000000,1590,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf"]
[null,null,"Product #","EFC CT1-13ET SIMpull PVC Jkt"]
[null,null,"Spec #",46302]
["CATALOG SPEC: EFC CT1- 13ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,95363899,"78 x 54",641,"N/A",0.995,155,165,10000,"No",0.828,11.94,66360,838,66360]
[1,95510499,"84 x 62",719,"N/A",1.035,175,185,10000,"No",0.868,12.419999999999998,83690,878,83690]
["1/0",95598999,"78 x 54",819,"N/A",1.075,200,215,8000,"Yes ",0.908,12.899999999999999,105600,918,105600]
["2/0","95-59-97-99","78 x 54",930,"N/A",1.115,230,245,8000,"Yes ",0.948,13.379999999999999,133100,958,133100]
["3/0","95-60-03-99","78 x 54",1071,"N/A",1.165,260,275,6000,"Yes ",0.998,13.98,167800,1008,167800]
["4/0","95-60-11-99","78 x 54",1238,"N/A",1.22,295,315,6000,"Yes ",1.053,14.64,211600,1063,211600]
[250,"95-60-29-99","78 x 54",1392,"N/A",1.275,325,345,5000,"Yes ",1.108,15.299999999999999,250000,1118,250000]
["350","95-60-37-99","78 x 54",1772,"N/A",1.38,390,415,4500,"Yes ",1.213,16.56,350000,1223,350000]
["500","95-60-45-99","72 x 42",2317,"N/A",1.505,465,500,3000,"Yes ",1.338,18.06,500000,1348,500000]
["600"]
["750","95-60-52-99","78 x 54",3313,"N/A",1.755,565,610,2500,"Yes ",1.525,21.06,750000,1535,750000]
["1000","95-60-60-99","78 x 54",4197,"N/A",1.908,640,690,2500,"Yes ",1.678,22.896,1000000,1688,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-20C (-4F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46103+CU+1C+115NLEPR+tape+CPE+5KV+133.pdf"]
[null,null,"Product #","CT1-09ET-C"]
[null,null,"Spec #",46103]
["CATALOG SPEC:  CT1- 09ET-C   CPE JACKET",{"$nulls":10},"CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,"55-05-12-99",null,294,"N/A",0.678,85,92,null,"No",0.52,8.136000000000001,26240,530,26240]
[4,"55-05-13-99",null,365,"N/A",0.725,110,120,null,"No",0.568,8.7,41740,578,41740]
[2,"55-05-14-99","64 x 54",468,"N/A",0.815,145,155,10000,"No",0.623,9.78,66360,633,66360]
[1,{"$nulls":5},170,180,null,null,0.663,0,83690,673,83690]
["1/0","55-05-15-99","78 x 42",660,"N/A",0.89,195,210,10000,"Yes ",0.703,10.68,105600,713,105600]
["2/0","55-05-16-99","84 x 54",769,"N/A",0.975,220,235,10000,"Yes ",0.743,11.7,133100,753,133100]
["3/0",null,"  ",null,null,null,250,270,null,null,0.793,0,167800,803,167800]
["4/0","55-05-18-99","84 x 54",1076,"N/A",1.08,290,310,8000,"Yes ",0.848,12.96,211600,858,211600]
[250,"55-05-19-99","78 x 54",1217,"N/A",1.14,320,345,7000,"Yes ",0.905,13.68,250000,915,250000]
["350","55-05-20-99","78 x 42",1592,"N/A",1.24,385,415,5000,"Yes ",1.008,14.879999999999999,350000,1018,350000]
["500","55-05-21-99","78 x 54",2137,"N/A",1.39,470,505,4000,"Yes ",1.133,16.68,500000,1143,500000]
["600"]
["750","55-05-22-99","78 x 54",3023,"N/A",1.58,585,630,2500,"Yes ",1.32,18.96,750000,1330,750000]
["1000","55-05-23-99","78 x 42",3887,"N/A",1.725,670,720,2000,"Yes ",1.465,20.700000000000003,1000000,1475,1000000]
[1250]
[1500]
[]
[]
[]
[]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-20C (-4F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46304+CU+1C+220NLEPR+tape+CPE+15KV+133.pdf"]
[null,null,"Product #","CT1-13ET-C"]
[null,null,"Spec #",46304]
["CATALOG SPEC:  CT1-13ET-C   CPE JACKET",{"$nulls":10},"CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,"55-05-02-99","84 x 62",672,"N/A",1.032,155,165,10000,"No",0.828,12.384,66360,838,66360]
[1,{"$nulls":5},175,185]
["1/0","55-05-03-99","84 x 62",845,"N/A",1.112,200,215,9000,"Yes",0.908,13.344000000000001,105600,918,105600]
["2/0","55-05-04-99","78 x 54",961,"N/A",1.157,230,245,8000,"Yes",0.948,13.884,133100,958,133100]
["3/0",{"$nulls":5},260,275,null,null,0.998,0,167800,1008,167800]
["4/0","55-05-05-99","78 x 54",1278,"N/A",1.267,295,315,6000,"Yes",1.053,15.203999999999999,211600,1063,211600]
[250,"55-05-06-99","78 x 54",1452,"N/A",1.337,325,345,5000,"Yes",1.108,16.044,250000,1118,250000]
["350","55-05-07-99","78 x 54",1833,"N/A",1.437,390,415,4500,"Yes",1.213,17.244,350000,1223,350000]
["500","55-05-08-99","78 x 42",2388,"N/A",1.567,465,500,3000,"Yes",1.338,18.804,500000,1348,500000]
["600"]
["750","55-05-10-99","78 x 54",3394,"N/A",1.807,565,610,2500,"Yes",1.525,21.683999999999997,750000,1535,750000]
["1000","55-05-11-99","78 x 54",4305,"N/A",1.972,640,690,2500,"Yes",1.678,23.664,1000000,1688,1000000]
[1250]
[1500]
[]
[]
[]
["hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SOLONON PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46104+CU+1C+115NLEPR+tape+LSZH+5KV+133.pdf"]
[null,null,"Product #","CT1-09ET-S"]
[null,null,"Spec #",46104]
["CATALOG SPEC:  CT1-09ET-S  SOLONON JACKET",{"$nulls":10},"CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,294,"N/A",0.678,85,92,null,"No",0.588,8.136000000000001,26240,598,26240]
[4,null,null,365,"N/A",0.725,110,120,null,"No",0.635,8.7,41740,645,41740]
[2,"89-06-53-99","84 x 62",468,"N/A",0.815,145,155,10000,"No",0.655,9.78,66360,665,66360]
[1,null,null,571,"N/A",0.85,170,180,null,"No",0.69,10.2,83690,700,83690]
["1/0","55-07-78-99","84 x 62",660,"N/A",0.89,195,210,9000,"Yes",0.73,10.68,105600,740,105600]
["2/0","55-07-79-99","78 x 54",769,"N/A",0.975,220,235,8000,"Yes",0.775,11.7,133100,785,133100]
["3/0",null,"  ",903,"N/A",1.025,250,270,null,"Yes",0.825,12.299999999999999,167800,835,167800]
["4/0","55-07-81-99","78 x 54",1076,"N/A",1.08,290,310,6000,"Yes",0.88,12.96,211600,890,211600]
[250,null,"78 x 54",1217,"N/A",1.14,320,345,5000,"Yes",0.94,13.68,250000,950,250000]
["350","89-06-54-99","78 x 54",1582,"N/A",1.24,385,415,4500,"Yes",1040,14.879999999999999,350000,1050,350000]
["500","55-07-83-99","78 x 42",2137,"N/A",1.39,470,505,3000,"Yes",1.19,16.68,500000,1200,500000]
["600",null,"  "]
["750","55-19-96-99","78 x 54",3023,"N/A",1.58,585,630,2500,"Yes",1.38,18.96,750000,1390,750000]
["1000","55-19-95-99","78 x 54",3887,"N/A",1.725,670,720,2500,"Yes",1.625,20.700000000000003,1000000,1635,1000000]
[1250]
[1500]
[]
[]
[]
["Payne"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SOLONON PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46305+CU+1C+220NLEPR+tape+LSZH+15KV+133.pdf"]
[null,null,"Product #","CT1-13ET-S"]
[null,null,"Spec # ",46305]
["CATALOG SPEC:  CT1-13ET-S  SOLONON JACKET",{"$nulls":10},"CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,"55-07-82-99","84 x 62",645,"N/A",1.032,155,165,10000,"No",0.828,12.384,66360,875,66360]
[1,null,"  ",null,"N/A",null,175,185,null,null,null,0,83690,915]
["1/0","55-07-84-99","84 x 62",814,"N/A",1.112,200,215,9000,"Yes",0.908,13.344000000000001,105600,955,105600]
["2/0","55-07-85-99","78 x 54",930,"N/A",1.157,230,245,8000,"Yes",0.948,13.884,133100,1000,133100]
["3/0",null,"  ",null,null,null,260,275,null,null,0.998,0,167800,1050,167800]
["4/0","55-07-86-99","78 x 54",1253,"N/A",1.267,295,315,6000,"Yes",1.053,15.203999999999999,211600,1110,211600]
[250,"55-07-87-99","78 x 54",1423,"N/A",1.337,325,345,5000,"Yes",1.108,16.044,250000,1180,250000]
["350","55-07-88-99","78 x 54",1803,"N/A",1.437,390,415,4500,"Yes",1.213,17.244,350000,1280,350000]
["500","55-07-89-99","78 x 42",2355,"N/A",1.567,465,500,3000,"Yes",1.338,18.804,500000,1410,500000]
["600",null,"  "]
["750","55-07-90-99","78 x 54",3355,"N/A",1.807,565,610,2500,"Yes",1.525,21.683999999999997,750000,1590,750000]
["1000",null,null,4294,"N/A",1.972,640,690,null,"Yes",1.678,23.664,1000000,1755,1000000]
[1250]
[1500]
[]
[]
[]
["Sheets",{"$nulls":15},"Sheets"]
[null,null,"CU or AL","CU",{"$nulls":14},"CU or AL","CU"]
[null,null,"Conductor count","1 / C",{"$nulls":14},"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","25kV 320 MIL EPR 133% CU Tape",{"$nulls":14},"Voltage / Ins  level / shield","25kV 260 MIL EPR 100% CU Tape"]
[null,null,"Armor","None",{"$nulls":14},"Armor","None"]
[null,null,"Jacket","SIMpull PVC",{"$nulls":14},"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000,{"$nulls":14},"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 75kV -dc (cond-grd), normally for 15 minutes. ",{"$nulls":14},"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 75kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)",{"$nulls":14},"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec46000/SPEC46502+CU+1C+320NLEPR+tape+PVC-SIM+25KV+133.pdf",{"$nulls":14},"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46501+CU+1C+260NLEPR+tape+PVC-SIM+25KV+100.pdf"]
[null,null,"Product #",{"$nulls":15},"Product #","EFC 15ET SIMpull "]
[null,null,"Spec #",46502,{"$nulls":14},"Spec #",46501]
[{"$nulls":11},"CU 1 / C 25kV 320 MIL EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed",{"$nulls":4},"CATALOG SPEC: EFC 15 - ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 25kV 260 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions",null,"  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",{"$nulls":15},"14 Str"]
["12 Str",{"$nulls":15},"12 Str"]
["10 Str",{"$nulls":15},"10 Str"]
["8",{"$nulls":15},"8"]
[6,{"$nulls":5},90,97,{"$nulls":8},6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125,{"$nulls":8},4,{"$nulls":5},115,125]
[2,{"$nulls":5},155,165,{"$nulls":8},2,{"$nulls":5},155,165]
[1,null,null,909,"N/A",1.239,175,185,null,"No",1.059,14.868000000000002,83690,1.069,83690,null,1,95725899,null,790,"N/A",1.11,175,185,null,"No",0.943,13.32,83690,953,83690]
["1/0",64461499,null,1009,"N/A",1.279,200,215,10000,"Yes",1.099,15.347999999999999,105600,1.109,105600,null,"1/0",55473399,"96 x 55",887,"N/A",1.15,200,215,10000,"No",0.983,13.799999999999999,105600,993,105600]
["2/0",64461599,null,1129,"N/A",1.322,230,245,null,"Yes",1.142,15.864,133100,1.152,133100,null,"2/0",55573099,"  ",1000,"N/A",1.19,230,245,null,"No",1.023,14.28,133100,1033,133100]
["3/0",64461699,null,1278,"N/A",1.373,260,275,null,"Yes",1.193,16.476,167800,1.203,167800,null,"3/0",55428799,"  ",1144,"N/A",1.24,260,275,null,"No",1.073,14.879999999999999,167800,1083,167800]
["4/0",64461899,null,1459,"N/A",1.429,295,315,7000,"Yes",1.249,17.148,211600,1.259,211600,null,"4/0",95726699,"92 x 55",1319,"N/A",1.295,295,315,7000,"No",1.128,15.54,211600,1138,211600]
[250,64461999,null,1622,"N/A",1.484,325,345,6000,"Yes",1.304,17.808,250000,1.314,250000,null,250,55427999,"92 x 55",1479,"N/A",1.352,325,345,6000,"No",1.185,16.224,250000,1195,250000]
["350",64462199,null,2015,"N/A",1.587,390,415,5000,"Yes",1.407,19.044,350000,1.417,350000,null,"350",55293599,"84 x 62",1863,"N/A",1.455,390,415,5000,"No",1.288,17.46,350000,1298,350000]
["500",64462399,null,2582,"N/A",1.715,465,500,2500,"Yes",1.535,20.580000000000002,500000,1.545,500000,null,"500",55451999,"72 x 44",2415,"N/A",1.58,465,500,2500,"No",1.413,18.96,500000,1423,500000]
["600",64462499,null,3062,"N/A",1.861,null,null,2500,"Yes",1.621,22.332,600000,1.631,600000,null,"600",null,"  "]
["750",64462699,null,3614,"N/A",1.963,565,610,2500,"Yes",1.723,23.556,750000,1.733,750000,null,"750",55574899,"78 x 54",3426,"N/A",1.83,565,610,2500,"No",1.6,21.96,750000,1610,750000]
["1000",64462799,null,4514,"N/A",2.112,640,690,2000,"Yes",1.872,25.344,1000000,1.882,1000000,null,"1000",60900899,"78 x 54",4320,"N/A",1.983,640,690,2000,"No",1.753,23.796,1000000,1763,1000000]
[1250,{"$nulls":15},1250]
[1500,{"$nulls":15},1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","35kV 345 MIL EPR 100% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46701+CU+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf"]
[null,null,"Product #","EFC CT1 19ET SIMpull PVC JKT"]
[null,null,"Spec #",46701]
["CATALOG SPEC:  EFC CT1 19 - ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,{"$nulls":5},155,165]
[1,{"$nulls":5},175,185]
["1/0",55583999,"78 x 54",1071,"N/A",1.32,200,215,5000,"No",1.153,15.84,105600,1163,105600]
["2/0",55584799,"78 x 54",1189,"N/A",1.36,230,245,5000,"No",1.193,16.32,133100,1203,133100]
["3/0",55585499,"84 x 62",1340,"N/A",1.41,260,275,5000,"No",1.23,16.919999999999998,167800,1253,167800]
["4/0",55586299,"96 x 63",1523,"N/A",1.465,295,315,7000,"No",1.298,17.580000000000002,211600,1308,211600]
[250,55587099,"84 x 62",1688,"N/A",1.52,325,345,6000,"No",1.355,18.240000000000002,250000,1365,250000]
["350",55198699,"78 x 54",2089,"N/A",1.625,390,415,3000,"No",1.458,19.5,350000,1468,350000]
["500",55588899,"78 x 54",2761,"N/A",1.813,465,500,2500,"No",1.583,21.756,500000,1593,500000]
["600",60898499,"78 x 54",3669,"N/A",null,null,null,2500,"No",null,0,600000,null,600000]
["750",95731699,"84 x 62",3718,"N/A",2.008,565,610,2500,"No",1.778,24.096,750000,1788,750000]
["1000",60899299,"84 x 62",4620,"N/A",2.153,640,690,2000,"No",1.923,25.836,1000000,1933,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","35kV 420 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46702+CU+1C+420NLEPR+tape+PVC-SIM+35KV+133.pdf"]
[null,null,"Product #","EFC CT1-21ET SIMpull PVC Jkt"]
[null,null,"Spec #",46702]
["CATALOG SPEC: EFC CT1 - 21ET SIMpull-PVC Jkt",{"$nulls":10},"CU 1 / C 35kV 420 Mil EPR 133% CU Tape Non Armored SIMpul- PVC Jacketed"]
[]
[]
["  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(77) @ 90 C","Duct 310.60(C)(77) @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,{"$nulls":5},90,97]
[4,{"$nulls":5},115,125]
[2,{"$nulls":5},155,165]
[1,{"$nulls":5},175,185]
["1/0","89-00-65-99","96 x 55",1254,"N/A",1.465,200,215,6000,"Yes",1.298,17.580000000000002,105600,1308,105600]
["2/0",null,"  ",1378,"N/A",1.505,230,245,null,"Yes",1.338,18.06,133100,1348,133100]
["3/0",null,"  ",null,null,null,260,275]
["4/0","89-00-66-99","92 x 55",1717,"N/A",1.61,295,315,4500,"Yes",1.443,19.32,211600,1453,211600]
[250,null,"  ",1991,"N/A",1.73,325,345,null,"Yes",1.5,20.759999999999998,250000,1510,250000]
["350","89-00-67-99","84 x 62",2407,"N/A",1.833,390,415,3000,"Yes",1.603,21.996,350000,1613,350000]
["500","89-00-68-99","84 x 62",3011,"N/A",1.965,465,500,2500,"Yes",1.735,23.580000000000002,500000,1745,500000]
["600",null,"  "]
["750","89-00-84-99","84 x 62",3979,"N/A",2.153,565,610,2000,"Yes",1.923,25.836,750000,1933,750000]
["1000","89-00-85-99","78 x 54",4898,"N/A",2.298,640,690,1500,"Yes",2.068,27.576,1000000,2078,1000000]
[1250]
[1500]
[]
[]
[]
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46202+CU+3C+115NLEPR+tape+PVC+5KV+133.pdf"]
[null,null,"Product #","EFC CT3-09ET PVC Jkt"]
[null,null,"Spec # ",46202]
["CATALOG SPEC EFC CT3 - 09ET PVC Jkt",{"$nulls":10},"CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Non Armored  PVC Jacketed"]
["3/C, 5KV, 115 MIL EPR, 25% OVERLAP TAPE SHIELD, GW, PVC JACKET, CT RATED, MV-105"]
[" 3/C    SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,1007,6,1.329,95,92,null,"Yes",0.52,9.302999999999999,26240,530,157440]
[4,null,null,1234,6,1.427,125,120,null,"Yes",0.568,9.989,41740,578,151460]
[2,95629299,"84 x 62",1575,6,1.551,160,165,5000,"Yes",0.623,10.857,66360,633,225320]
[1,55814899,"96 x 55",1836,4,1.637,185,185,5000,"Yes",0.663,11.459,83690,673,292810]
["1/0",95630099,"84 x 62",2227,4,1.787,210,215,3500,"Yes",0.703,12.509,105600,713,358540]
["2/0",95837199,"84 x 62",2570,4,1.873,235,245,3000,"Yes",0.743,13.111,133100,753,441040]
["3/0",55817199,"78 x 54",3006,3,1.981,270,280,2000,"Yes",0.793,13.867,167800,803,556020]
["4/0",95745699,"78 x 54",3546,3,2.1,305,320,2000,"Yes",0.848,14.700000000000001,211600,858,687420]
[250,95838699,"84 x 62",4088,3,2.236,335,350,2000,"Yes",0.905,15.652000000000001,250000,915,802620]
["350",95517999,"78 x 54",5240,2,2.457,400,430,1500,"Yes",1.008,17.198999999999998,350000,1018,1116360]
["500",95839799,"104 x 57",7103,1,2.78,485,525,2000,"Yes",1.133,19.459999999999997,500000,1143,1583690]
["750",55749699,"96 x 63",9958,"1/0",3.185,585,635,1250,"Yes",1.32,22.295,750000,1330,2355600]
["1000",{"$nulls":9},1.465,null,1000000]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46402+CU+3C+220NLEPR+tape+PVC+15KV+133.pdf"]
[null,null,"Product #","EFC CT3-13ET PVC Jkt"]
[null,null,"Spec #",46402]
["CATALOG SPEC EFC CT3 - 13ET PVC Jkt",{"$nulls":10},"CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Non Armored PVC Jacketed"]
["3/C, 15KV, 220 MILS EPR, 25% OVERLAP TAPE SHIELD, GW, PVC JACKET, CT RATED, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,95649099,"96 x 55",2252,6,2.057,160,165,3000,"Yes",0.828,14.399,66360,838,225320]
[1,95829899,"96 x 55",2566,4,2.143,185,185,3000,"Yes",0.868,15.000999999999998,83690,878,292810]
["1/0",95830699," ",2881,4,2.229,210,215,3000,"Yes",0.908,15.603000000000002,105600,918,358540]
["2/0",55825499,"96 x 63",3244,4,2.316,235,245,3000,"Yes",0.948,16.212,133100,958,441040]
["3/0",95831499,"96 x 63",3724,3,2.424,270,280,2500,"Yes",0.998,16.968,167800,1008,556020]
["4/0",95628499,"96 x 55",4283,3,2.543,305,320,2000,"Yes",1.053,17.801000000000002,211600,1063,687420]
[250,55828899,"96 x 63",4849,3,2.673,335,350,1750,"Yes",1.108,18.711,250000,1118,802620]
["350",95832299,"96 x 63",6232,2,2.953,400,430,1500,"Yes",1.213,20.671,350000,1223,1116360]
["500",95833099,"96 x 63",8056,1,3.223,485,525,1000,"Yes",1.338,22.561,500000,1348,1583690]
["750",55831299,"108 x 71",11025,"1/0",3.628,585,635,1000,"Yes",1.525,25.396,750000,1535,2355600]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","2.4 kV Non Shielded"]
[null,null,"Armor","None"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address"]
[null,null,"Product #","EFC CT3-09ENS PVC Jkt"]
[null,null,"Spec #"]
["CATALOG SPEC EFC CT3 - 09ENS PVC Jkt",{"$nulls":10},"CU 3 / C WG 2.4 kV Non Shielded Non Armored PVC Jacketed"]
["3/C, 5KV, 115 MIL  EPR, NON-SHIELDED, GW, PVC JACKET, CT-RATED, MV-90"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @105 C","Conduit in Air 310.75 @105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,747,6,1.123,84,77,null,"Yes",null,7.861,26240,null,104960]
[4,null,null,959,6,1.223,110,100,null,"Yes",null,8.561,41740,null,151460]
[2,"60-04-29-99","78 x 54",1251,6,1.35,145,135,5000,"Yes",null,9.450000000000001,66360,null,225320]
[1]
["1/0","60-04-11-99","78 x 54",1767,4,1.519,190,185,3500,"Yes",null,10.633,105600,null,358540]
["2/0","60-04-03-99",null,2098,4,1.614,220,210,null,"Yes",null,11.298,133100,null,441040]
["3/0"]
["4/0","60-03-95-99","78 x 54",3123,3,1.903,285,285,2500,"Yes",null,13.321,211600,null,687420]
[250,"61-01-70-99","  ",3598,3,2.037,315,315,null,"Yes",null,14.259,250000,null,802620]
["350","60-04-45-99","92 x 55",4752,2,2.258,380,390,2500,"Yes",null,15.806000000000001,350000,null,1116360]
["500","60-03-87-99","92 x 55",6444,1,2.536,460,475,1750,"Yes",null,17.752,500000,null,1500000]
["750"]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V"]
[null,null,"Armor","Aluminum (AIA)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45301+CU+3C+XLPE+XHHW+AIA+PVC+600V+W1CUGW.pdf"]
[null,null,"Product #","AL01XXH"]
[null,null,"Spec #",45301]
["CATALOG SPEC  AL01 - XXH",{"$nulls":10},"CU 3 / C WG 600V AIA Armored PVC Jacketed"]
["3/C, 600 VOLT,  XHHW, GW, AIA, BLACK PVC JACKET"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter",null,"Free Air 90 C 310.3","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8","60-69-39-99","66 x 36",405,10,0.82,null,59,6000,"Yes",null,5.739999999999999,16510,null,49530]
[6,"60-69-47-99","66 x 42",550,8,0.896,null,79,6000,"Yes",null,6.272,26240,null,95230]
[4,"60-69-54-99","64 x 54",727,8,0.995,null,104,6000,"Yes",null,6.965,41740,null,141730]
[2,56046699,"66 x 42",1048,6,1.118,null,138,4000,"Yes",null,7.8260000000000005,66360,null,225320]
[1,null,"  "]
["1/0",56047499,"78 x 42",1533,6,1.344,null,186,4000,"Yes",null,9.408000000000001,105600,null,343040]
["2/0",56048299,"78 x 54",1823,6,1.437,null,215,4000,"Yes",null,10.059000000000001,133100,null,425540]
["3/0",89033999,"92 x 55",2262,4,1.543,null,249,5000,"Yes",null,10.801,167800,null,545140]
["4/0","38-36-79-99","78 x 54",2814,4,1.784,null,287,3000,"Yes",null,12.488,211600,null,676540]
[250,"60-13-77-99","84 x 62",3275,4,1.931,null,320,3000,"Yes",null,13.517,250000,null,791740]
["350","38-36-46-99","96 x 63",4396,3,2.153,null,394,3000,"Yes",null,15.071,350000,null,1102620]
["500","38-06-18-99","92 x 55",6104,2,2.462,null,487,2000,"Yes",null,17.234,500000,null,1566360]
["750",89040599,"108 x 73",8860,1,2.915,null,615,2000,"Yes",null,20.405,750000,null,2250000]
["1000",null,"  "]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","2.4 kV Non Shielded"]
[null,null,"Armor","Aluminum (AIA)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46026+CU+3C+115EPR+none+AIA+PVC+2.4KV+100.pdf"]
[null,null,"Product #","AL09ENS"]
[null,null,"Spec #",46026]
["CATALOG SPEC AL-09ENS",{"$nulls":10},"CU 3 / C WG 2.4 kV Non Shielded AIA Armored PVC Jacketed"]
["3/C, 5KV, 115 MILS EPR, NON-SHIELDED, GW, AIA, YELLOW PVC JKT, MV-90"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83 @ 90 C","Free Air 90 C 310.71","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,801,6,1.214,105,79,null,"Yes",null,8.498,26240,null,104960]
[4,null,null,1006,6,1.312,135,105,null,"Yes",null,9.184000000000001,41740,null,151460]
[2,"89-00-86-99","78 x 42",1321,6,1.436,180,140,3100,"Yes",null,10.052,66360,null,225320]
[1,"55-22-54-99","78 x 42",1589,4,1.522,200,160,3100,"Yes",null,10.654,83690,null,292810]
["1/0","60-64-67-99","72 x 42",1930,4,1.729,230,185,2000,"Yes",null,12.103000000000002,105600,null,358540]
["2/0","55-22-12-99","84 x 54",2260,4,1.815,260,215,3000,"Yes",null,12.705,133100,null,441040]
["3/0",null,"  "]
["4/0","55-22-13-99","84 x 54",3186,3,2.042,335,285,2500,"Yes",null,14.293999999999999,211600,null,687420]
[250,"55-22-55-99","84 x 54",3637,3,2.161,365,320,2100,"Yes",null,15.127,250000,null,802620]
["350","55-15-26-99","84 x 62",4870,2,2.417,440,395,1500,"Yes",null,16.918999999999997,350000,null,1116360]
["500","89-06-45-99","96 x 63",6556,1,2.687,530,485,2100,"Yes",null,18.808999999999997,500000,null,1583690]
["750","55-22-56-99","92 x 55",9336,"1/0",3.096,650,615,1050,"Yes",null,21.672,750000,null,2355600]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","Aluminum (AIA)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46254+CU+3C+115NLEPR+tape+AIA+PVC+5KV+133.pdf"]
[null,null,"Product #","AL09ET"]
[null,null,"Spec #",46254]
["CATALOG SPEC   AL - 09ET",{"$nulls":10},"CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
["3/C  5KV / 8KV, 115 MILS  EPR, 25% OVERLAP TAPE SHIELD, GW, AIA, YELLOW PVC JACKET, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83 @ 105C","Free Air 105 C 310.71","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
["2",55660599,"92 x 55",1821,6,1.826,200,185,4000,"Yes ",0.623,12.782,66360,633,225320]
[1,55661399,"  ",2094,4,1.912,225,210,null,"Yes ",0.663,13.384,83690,673,292810]
["1/0",55662199,"96 x 63",2395,4,1.999,255,240,4000,"Yes ",0.703,13.993,105600,713,358540]
["2/0",55663999,"96 x 63",2744,4,2.085,290,275,4000,"Yes ",0.743,14.594999999999999,133100,753,441040]
["3/0",55664799,"96 x 55",3189,3,2.193,330,315,3000,"Yes ",0.793,15.351,167800,803,556020]
["4/0",55665499,"96 x 55",3783,3,2.312,375,360,2500,"Yes ",0.848,16.183999999999997,211600,858,687420]
[250,55666299,"  ",4285,3,2.461,410,400,null,"Yes ",0.905,17.227,250000,915,802620]
["350",55667099,"92 x 55",5508,2,2.687,495,490,1500,"Yes ",1.008,18.808999999999997,350000,1018,1116360]
["500",55668899,"96 x 63",7262,1,2.957,590,600,1600,"Yes ",1.133,20.698999999999998,500000,1143,1583690]
["750",55669699,"104 x 57",10199,"1/0",3.382,720,745,1250,"Yes ",1.32,23.674,750000,1330,2355600]
["1000"]
{"$rows_empty":7}
["Chris T."]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","Aluminum (AIA)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46453+CU+3C+220NLEPR+tape+AIA+PVC+15KV+133.pdf"]
[null,null,"Product #","AL13ET"]
[null,null,"Spec # ",46453]
["CATALOG SPEC   AL - 13ET",{"$nulls":10},"CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
["3/C, 15KV, 133%, 220 MILS EPR, 25% OVERLAP TAPE SHIELD, GW, AIA, RED PVC JACKET, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83","Free Air 105 C 310.71","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
["2",55167199,"96 x 63",2440,6,2.269,200,185,3500,"Yes ",0.828,15.883000000000001,66360,838,225320]
[1,55684499,"108 x 71",2761,4,2.355,225,210,3500,"Yes ",0.868,16.485,83690,878,292810]
["1/0",55695199,"96 x 55",3150,4,2.471,255,240,2500,"Yes ",0.908,17.297,105600,918,358540]
["2/0",95788699,"96 x 63",3522,4,2.558,290,275,2500,"Yes ",0.948,17.906,133100,958,441040]
["3/0",55696999,null,4014,3,2.666,330,315,null,"Yes ",0.998,18.662,167800,1008,556020]
["4/0",55164899,"108 x 71",4585,3,2.785,375,360,2500,"Yes ",1.053,19.495,211600,1063,687420]
[250,44727699,"108 x 71",5095,3,2.903,410,400,2500,"Yes ",1.108,20.321,250000,1118,802620]
["350",55161499,"108 x 71",6399,2,3.13,495,490,1600,"Yes ",1.213,21.91,350000,1223,1116360]
["500","40-91-69-99","108 x 71",8299,1,3.42,590,600,1600,"Yes ",1.338,23.939999999999998,500000,1348,1583690]
["750",55697799,"108 x 71",11294,"1/0",3.825,720,745,1250,"Yes ",1.525,26.775000000000002,750000,1535,2355600]
["1000",{"$nulls":9},1.678,20.136,1000000]
{"$rows_empty":7}
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","4 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V"]
[null,null,"Armor","Armor-X (CCW)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45352+CU+4C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf"]
[null,null,"Product #","HLX01XXH"]
["CATALOG SPEC  HLX01XXH",null,"Spec #",45352]
["600 Volt, XLP, GW, ARMOR-X, -40C PVC Jkt. Type MC-HL, ABS Rated",{"$nulls":10}," CU 4 / C WG Armor-X (CCW) Armored PVC Jacketed"]
[]
["4/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter",null,"4/C @ 90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",55058799,"50 x 34",202,"3 x #18",0.65,null,20,5000,"Yes",null,4.55,4110,null,21300]
["12 Str",55058999,"50 x 34",252,"3 x #16",0.68,null,24,5000,"Yes",null,4.760000000000001,6530,null,33860]
["10 Str",55059299,"58 x 37",332,"3 x #14",0.73,null,32,5000,"Yes",null,5.109999999999999,10380,null,53850]
["8","89-05-27-99","58 x 37",465,"1 x #10",0.9,null,44,4000,"Yes",null,6.3,16510,null,76420]
[6,89052899,"58 x 37",640,"1 x #8",1.01,null,60,3000,"Yes",null,7.07,26240,null,121470]
[4,89052999,"66 x 36",885,"1 x #8",1.11,null,76,3000,"Yes",null,7.7700000000000005,41740,null,183470]
[2,89053099,"64 x 54",1291,"1 x #6",1.32,null,104,3000,"Yes",null,9.24,66360,null,291680]
[1]
["1/0",89053199,"66 x 42",1903,"1 x #6",1.57,null,136,2000,"YES",null,10.99,105600,null,448640]
["2/0",89053299,"64 x 54",2376,"1 x #4",1.71,null,156,2000,"YES",null,11.969999999999999,133100,null,574140]
["3/0",{"$nulls":8},"YES",null,0,167800]
["4/0",89053399,"78 x 54",3470,"1 x #4",1.99,null,208,2000,"YES",null,13.93,211600,null,888140]
[250,89053499,"108 x 73",4052,"1 x #4",2.16,null,232,4000,"YES",null,15.120000000000001,250000,null,1041740]
["350",89053599,"78 x 54",5511,"1 x #3",2.44,null,280,1500,"YES",null,17.08,350000,null,1452620]
["500",89053699,"96 x 55",7721,"1 x #2",2.82,null,344,1500,"YES",null,19.74,500000,null,2066360]
["750",89053799,"108 x 73",11964,"1 x #1 ",3.39,null,428,1500,"YES",null,23.73,750000,null,3000000]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","600V"]
[null,null,"Armor","Armor-X (CCW)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45351+CU+3C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf"]
[null,null,"Product #","HLX01XXH"]
[null,null,"Spec #",45351]
["CATALOG SPEC  HLX01XXH",{"$nulls":10},"CU 3 / C WG 600V Armor-X (CCW) Armored PVC Jacketed"]
["600 Volt, XLP, GW, ARMOR-X, -40C PVC Jkt. Type MC-HL, ABS Rated"]
["3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter",null,"90 C 310.16","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",55058699,"42 x 33",175,"3 x #18",0.6,null,25,5000,"Yes ",null,4.2,4110,null,17190]
["12 Str",55058899,"50 x 34",221,"3 x #16",0.65,null,30,5000,"Yes ",null,4.55,6530,null,27330]
["10 Str",55059199,"58 x 37",283,"3 x #14",0.68,null,40,5000,"Yes ",null,4.760000000000001,10380,null,53850]
["8",55059399,"58 x 37",405,"3 x #14",0.85,null,55,5000,"Yes ",null,5.95,16510,null,61860]
[6,89051399,"66 x 36",541,"3 x #12",0.9,null,75,5000,"Yes ",null,6.3,26240,null,98310]
[4,89051499,"66 x 42",698,"3 x #12",1.01,null,95,5000,"Yes ",null,7.07,41740,null,144810]
[2,89051599,"64 x 54",1043,"3 x #10",1.15,null,130,5000,"Yes ",null,8.049999999999999,66360,null,230220]
[1,null,"  "]
["1/0",89051699,"64 x 54",1675,"3 x #10",1.45,null,170,3000,"YES",null,10.15,105600,null,347940]
["2/0",89051799,"78 x 42",1857,"3 x# 8",1.57,null,195,3000,"YES",null,10.99,133100,null,448830]
["3/0",89051899,"78 x 54",2344,"3x #8",1.66,null,225,3500,"YES",null,11.62,167800,null,552930]
["4/0",89051999,"78 x 54",2792,"3 x #8",1.79,null,260,3000,"YES",null,12.530000000000001,211600,null,684330]
[250,89052099,"78 x 54",3277,"3 x #8",1.99,null,290,2000,"YES",null,13.93,250000,null,799530]
["350",89052199,"78 x 42",4420,"3 x #6",2.32,null,350,1500,"YES",null,16.24,350000,null,1128720]
["500",89052299,"84 x 54",6001,"3 x #6",2.58,null,430,1500,"YES",null,18.060000000000002,500000,null,1578720]
["750",89052399,"92 x 55",9375,"3 x #4",3.13,null,535,1000,"YES",null,21.91,750000,null,2328720]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","2.4 kV Non Shielded"]
[null,null,"Armor","Armor-X (CCW)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46027+CU+3C+90EPR+none+ARMOR-X+PVC+2.4KV+100.pdf"]
[null,null,"Product #","XAL07ENS"]
[null,null,"Spec # ",46027]
["CATALOG SPEC  XAL-07ENS",{"$nulls":10},"CU 3 / C WG 2.4 kV Non Shielded Armor-X (CCW) Armored PVC Jacketed"]
["3/C, 5KV, 090 Mils EPR, Non-Shield, 3xGW, Armor-X, -40 C Yellow PVC, Type MC, ABS Rated"]
["3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83 @ 90C","Free Air 105 C 310.71 @ 90C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,838,"3X10",1.32,105,79,null,"YES",null,9.24,26240,null,109860]
[4,null,null,1071,"3X10",1.45,135,105,null,"YES",null,10.15,41740,null,156360]
[2,89061599,"78 x 42",1390,"3x10",1.57,180,140,3000,"YES",null,10.99,66360,null,199080]
[1,null,"  "]
["1/0",89061699,"78 x 42",1920,"3x8",1.71,230,185,2500,"YES",null,11.969999999999999,105600,null,316800]
["2/0",89061799,"78 x 42",2243,"3x8",1.88,260,215,2000,"YES",null,13.16,133100,null,399300]
["3/0",null,"  "]
["4/0",89061899,"92 x 55",3287,"3x6",2.16,335,285,2500,"YES",null,15.120000000000001,211600,null,634800]
[250,89061999,"78 x 54",3688,"3x6",2.32,365,320,2000,"YES",null,16.24,250000,null,750000]
["350",89062099,"96 x 55",4961,"3x6",2.58,440,395,2000,"YES",null,18.060000000000002,350000,null,1050000]
["500",89062199,"96 x 55",6571,"3x4",2.82,530,485,1500,"YES",null,19.74,500000,null,1500000]
["750",89062299,"96 x 63",9700,"3x4",3.37,650,615,1000,"YES",null,23.59,750000,null,2250000]
["1000"]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","Armor-X (CCW)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46255+CU+3C+115NLEPR+tape+ARMOR-X+PVC+5KV+133.pdf"]
[null,null,"Product #","HLX09ET"]
[null,null,"Spec #",46255]
["CATALOG SPEC # HLX-09ET",{"$nulls":10},"CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
["3/C, 5/8KV, 115 Mils EPR, 25% Overlap Tape Shield, GW, ARMOR-X, - 40 C,"]
["3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83 @ 105C","Free Air 105 C 310.71@ 105C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6,null,null,1158,6,1.57,115,88,null,"YES",0.52,10.99,26240,530,104960]
[4,null,null,1460,6,1.71,150,115,null,"YES",0.565,11.969999999999999,41740,575,151460]
[2,89063699,"78 x 54",1797,6,1.88,190,154,2500,"YES",0.623,13.16,66360,633,225320]
[1,89063799,"92 x 55",2066,4,1.965,215,180,3500,"YES",0.663,13.755,83690,673,292810]
["1/0",89063899,"78 x 54",2368,4,1.99,245,205,2000,"YES",0.703,13.93,105600,713,358540]
["2/0",89063999,"78 x 54",2716,4,2.16,280,240,2000,"YES",0.743,15.120000000000001,133100,753,441040]
["3/0",null,"  "]
["4/0",89064099,"92 x 55",3808,3,2.44,360,320,2000,"YES",0.848,17.08,211600,858,687420]
[250,89064199,"90 x 68",4269,3,2.58,395,355,2050,"YES",0.905,18.060000000000002,250000,915,802620]
["350",89064299,"92 x 55",5483,2,2.82,475,440,1500,"YES",1.008,19.74,350000,1018,1116360]
["500",89064399,"96 x 55",7363,1,3.13,570,545,1300,"YES",1.133,21.91,500000,1143,1583690]
["750",89064499,"108 x 71",10741,"1/0",3.71,700,685,1000,"YES",1.32,25.97,750000,1330,2355600]
["1000",null,null,null," "," "," "]
{"$rows_empty":7}
["Hooper "]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","Armor-X (CCW)"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46454+CU+3C+220NLEPR+tape+ARMOR-X+PVC+15KV+133.pdf"]
[null,null,"Product #","HLX13ET"]
[null,null,"Spec #",46454]
["CATALOG SPEC # HLX-13ET",{"$nulls":10},"CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
["3/C, 15KV, 220 Mils EPR, 25% Overlap Tape Shield, GW, ARMOR-X, -40 C, RED PVC JKT, "]
["3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Direct Burial 310.83","Free Air 105 C 310.71","max length","CT Rated","Single O.D.over shield","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,89066399,"108 x 71",2540,6,2.44,200,185,3000,"YES",0.828,17.08,66360,838,225320]
[1]
["1/0"," "," ",3126,4,2.58,255,240,2000,"YES",0.908,18.060000000000002,105600,918,358540]
["2/0",89066599,"96 x 6 3",3533,4,2.7,290,275,2000,"YES",0.948,18.900000000000002,133100,958,441040]
["3/0",null,"  "]
["4/0",89066699,"108 x 71",4663,3,2.9,375,360,2000,"YES",1.053,20.3,211600,1063,687420]
[250,89066799,"108 x 71  ",5069,3,3.03,410,400,2000,"YES",1.108,21.209999999999997,250000,1120,802620]
["350",89066899,"108 x 71   ",6742,2,3.39,495,490,1500,"YES",1.213,23.73,350000,1223,1116360]
["500",89066999,"108 x 71  ",8674,1,3.71,590,600,1300,"YES",1.338,25.97,500000,1348,1500000]
["600"]
["750",55043999,"108 x 71",11666,"1/0",4.02,720,745,1005,"YES",1.525,28.139999999999997,750000,1475,2355600]
["1000"]
{"$rows_empty":7}
["Turner"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","1kV Non Shielded"]
[null,null,"Armor","Tech 90"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40 C (-40 F)"]
[null,null,"URL Address","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheetT90"]
[null,null,"Product #","3/C 1kV Tech 90"]
[null,null,"Spec #"]
[{"$nulls":11},"CU 3 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[]
["3/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Amps",null,"max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",56352299,"50 x 34",215,14,0.672,null,null,5000,null,null,6.720000000000001,4110,null,16440]
["12 Str",56352699,"50 x 34",252,12,0.71,null,null,5000,null,null,8.52,6530,null,26120]
["10 Str",56229799,"50 x 34",314,12,0.761,null,null,5000,null,null,9.132,10380,null,41520]
["8",56196399,"66 x 36",466,10,0.917,null,null,5000,null,null,11.004000000000001,16510,null,59910]
[6,56196599,"66 x 42",707,8,1.168,null,null,4000,null,null,14.015999999999998,26240,null,95230]
[4,56196799,"68 x 44",958,8,1.308,null,null,4000,null,null,15.696000000000002,41740,null,141730]
[2,56197299,"72 x 47",1305,6,1.43,null,null,4000,null,null,17.16,66360,null,225320]
[1,56197499,"78 x 54",1642,6,1.629,null,null,3000,null,null,24.435,83690,null,277310]
["1/0",56197699,"78 x 54",1913,6,1.713,null,null,3000,null,null,25.695,105600,null,343040]
["2/0",56194899,"78 x 54",2255,6,1.808,null,null,3000,null,null,27.12,133100,null,425540]
["3/0",56195099,"78 x 54",2695,4,1.916,null,null,2000,null,null,28.74,167800,null,545140]
["4/0",56195399,"78 x 54",3268,4,2.047,null,null,2000,null,null,30.705000000000002,211600,null,676540]
[250,56195599,"78 x 54",3885,4,2.254,null,null,1500,null,null,33.81,250000,null,791740]
["350",56195999,"72 x 55",5119,3,2.499,null,null,1500,null,null,37.485,350000,null,1102620]
["500",56196199,"84 x 54",6802,3,2.777,null,null,1500,null,null,41.655,500000,null,1552620]
["750",null,"  ",{"$nulls":9},750000]
["1000"]
{"$rows_empty":7}
["Allen"]
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","4 / C WG"]
[null,null,"Voltage / Ins  level / shield","1kV Non Shielded"]
[null,null,"Armor","Tech 90"]
[null,null,"Jacket","PVC"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","-40C (-40F)"]
[null,null,"URL Address","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet329"]
[null,null,"Product #","4/C 1kV Tech 90"]
[null,null,"Spec #"]
[{"$nulls":11},"CU 4 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[]
["4/C  SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Amps",null,"max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str",56178199,"50 x 34",240,14,0.705,null,null,5000,null,null,8.459999999999999,4110,null,16440]
["12 Str",56179499,"50 x 34",290,12,0.747,null,null,5000,null,null,8.964,6530,null,26120]
["10 Str",56179899,"50 x 34",367,12,0.804,null,null,5000,null,null,9.648,10380,null,47650]
["8",56196499,"66 x 36",553,10,0.975,null,null,4000,null,null,11.7,16510,null,66040]
[6,56196699,"64 x 54",888,8,1.283,null,null,4000,null,null,15.395999999999999,26240,null,121470]
[4,56196899,"64 x 54",1144,8,1.394,null,null,3000,null,null,16.727999999999998,41740,null,183470]
[2,56197399,"78 x 54",1574,6,1.531,null,null,3000,null,null,22.965,66360,null,291680]
[1,56197599,"84 x 62",2009,6,1.751,null,null,3000,null,null,26.264999999999997,83690,null,361000]
["1/0",56197899,"78 x 54",2351,6,1.845,null,null,2000,null,null,27.675,105600,null,448640]
["2/0",56194999,"78 x 54",2848,6,1.962,null,null,2000,null,null,29.43,133100,null,558640]
["3/0",56195299,"84 x 62",3412,4,2.082,null,null,2000,null,null,31.229999999999997,167800,null,712940]
["4/0",56195499,"96 x 55",4212,4,2.277,null,null,2000,null,null,34.155,211600,null,888140]
[250,56195699,"92 x 55",4878,4,2.464,null,null,1500,null,null,36.96,250000,null,1041740]
["350",56196099,"96 x 63",6416,3,2.712,null,null,1500,null,null,40.68,350000,null,1452620]
["500",56196299,"96 x 55",8602,3,3.024,null,null,1000,null,null,45.36,500000,null,2052620]
["750",null,"  ",{"$nulls":9},750000]
["1000"]
{"$rows_empty":11}
["Hooper"]
[null,null,"CU or AL","AL"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","600V XHHW ( XLP)"]
[null,null,"Armor","None"]
[null,null,"Jacket","None"]
[null,null,"Max Sidewall pressure ",500]
[null,null,"High Potential testing","N/A"]
[null,null,"Min Installation Temp","- 40C (-40F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45007+AL+1C+XLPE+XHHW+none+600V+.pdf"]
[null,null,"Product #","AL XHHW/CT"]
[null,null,"Spec #",45007]
["1/C 600V XHHW-2 CT RATED",{"$nulls":10},"AL 1 / C 600V XHHW ( XLP) Non Armored Non Jacketed"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","In Duct NEC 310.15 75 C","In Duct NEC 310.15 90 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2]
[1]
["1/0",56039799,"60 X 28",138,"N/A",0.449,120,135,15000,"Yes",null,1.796,105600,null,105600]
["2/0",56039699,"50 x 38",171,"N/A",0.489,135,150,10000,"Yes",null,1.956,133100,null,133100]
["3/0",null,"60 x 28",209,"N/A",0.536,155,175,10000,"Yes",null,2.144,167800,null,167800]
["4/0",56036199,"50 x 38",253,"N/A",0.588,180,205,7000,"Yes",null,2.352,211600,null,211600]
[250,56036299,"84 x 42",304,"N/A",0.653,205,230,10000,"Yes",null,2.612,250000,null,250000]
["350",56036399,"72 x 42",410,"N/A",0.749,250,280,7000,"Yes",null,2.996,350000,null,350000]
["500",56038099,"66 x 42",567,"N/A",0.869,310,350,4500,"Yes",null,3.476,500000,null,500000]
["600",56304499,"64 x 42",695,"N/A",0.976,340,385,4000,"Yes",null,3.904,600000,null,600000]
["750",56038199,"84 x 42",851,"N/A",1.071,385,435,3000,"Yes",null,5.3549999999999995,750000,null,750000]
["1000",56038299,"64 x 42",1110,"N/A",1.223,445,500,2500,"Yes",null,6.115,1000000,null,1000000]
[1250]
[1500]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","AL"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https ://s3.amazonaws.com/swspec/MV/SPEC46110+AL+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf"]
[null,null,"Product #","CT1A-09ET"]
[null,null,"Spec # ",46110]
["CATALOG SPEC: CT1A- 09ET SIMpull PVC Jkt",{"$nulls":10},"AL 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,56018299,"64 x 54",320,"N/A",0.774,115,125,10000,"No",0.56,9.288,66360,560,66360]
[1,56018199,"64 x 54",352,"N/A",0.807,130,140,10000,"No",0.59,9.684000000000001,83690,590,83690]
["1/0",55995399,"78 x 42",413,"N/A",0.873,150,160,10000,"YES",0.627,10.475999999999999,105600,627,105600]
["2/0",56011699,"78 x 54",460,"N/A",0.913,170,185,10000,"YES",0.667,10.956,133100,667,133100]
["3/0",56013399,"78 x 42",515,"N/A",0.958,195,210,8000,"YES",0.712,11.495999999999999,167800,712,167800]
["4/0",56013499,"78 x 54",583,"N/A",1.01,225,245,8000,"YES",0.762,12.120000000000001,211600,762,211600]
[250,56013799,"78 x 54",650,"N/A",1.065,250,270,7000,"YES",0.82,12.78,250000,820,250000]
["350",56013599,"72 x 47",766,"N/A",1.132,305,325,4000,"YES",0.915,13.584,350000,915,350000]
["500",56014799,"72 x 42",961,"N/A",1.25,370,400,3000,"YES",1.035,15,500000,1035,500000]
["600",57732199,"72 x 42",1162,"N/A",1.387,{"$nulls":5},16.644]
["750",56017999,"72 x 42",1353,"N/A",1.483,470,505,2500,"YES",1.22,17.796,750000,1220,750000]
["1000",56018099,"78 x 42",1668,"N/A",1.633,545,590,2000,"YES",1.36,19.596,1000000,1360,1000000]
[1250]
[1500]
{"$rows_empty":7}
["Hooper"]
[null,null,"CU or AL","AL"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46311+AL+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf"]
[null,null,"Product #","CT1A-13ET"]
[null,null,"Spec # ",46311]
["CATALOG SPEC: CT1A- 13ET",null,null,null,"CT RATED for Sizes 1/0 and Larger",{"$nulls":6},"AL 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,56019599,"78 x 54",504,"N/A",1.01,120,130,10000,"No",0.815,12.120000000000001,66360,815,66360]
[1,56020099,"84 x 62",540,"N/A",1.04,135,145,10000,"No",0.845,12.48,83690,845,83690]
["1/0",56021499,"78 x 54",585,"N/A",1.078,155,165,8000,"Yes ",0.882,12.936,105600,882,105600]
["2/0",56021599,"78 x 54",609,"N/A",1.088,175,190,8000,"Yes ",0.922,13.056000000000001,133100,922,133100]
["3/0",56021799,"78 x 54",670,"N/A",1.132,200,215,6000,"Yes ",0.967,13.584,167800,967,167800]
["4/0",56024699,"78 x 54",746,"N/A",1.185,230,245,6000,"Yes ",1.017,14.22,211600,1017,211600]
[250,56024799,"78 x 54",853,"N/A",1.27,250,270,5000,"Yes ",1.075,15.24,250000,1075,250000]
["350",56024899,"78 x 54",979,"N/A",1.337,305,330,4500,"Yes ",1.117,16.044,350000,1170,350000]
["500",56011799,"72 x 42",1259,"N/A",1.508,370,400,3000,"Yes ",1.29,18.096,500000,1290,500000]
["600",56321099,"72 x 42",1413,"N/A",1.593,null,null,3000,"Yes ",1.38,19.116,600000,1380,600000]
["750",56011899,"78 x 54",1717,"N/A",1.744,455,490,2500,"Yes ",1.47,20.928,750000,1470,750000]
["1000",56012499,"78 x 54",2090,"N/A",1.915,525,565,2500,"Yes ",1.62,22.98,1000000,1620,1000000]
[1250]
[1500]
{"$rows_empty":7}
["Allen"]
[null,null,"CU or AL","AL"]
[null,null,"Conductor count","1 / C"]
[null,null,"Voltage / Ins  level / shield","35kV 345 MIL EPR 100% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","SIMpull PVC"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-10C (14F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46709+AL+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf"]
[null,null,"Product #","CT1A-19ET"]
[null,null,"Spec #",46709]
["CATALOG SPEC: CT1A 19 -  ET",{"$nulls":10},"AL 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
[]
[]
["SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.60(C)(78) @ 90 C","Duct 310.60(C)(78) @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,{"$nulls":5},120,130]
[1,58374999,"78 x 54",null,null,null,135,145]
["1/0",null,"78 x 54",829,"N/A",1.295,155,165,5000,"Yes",1.128,15.54,105600,null,105600]
["2/0",{"$nulls":5},175,190]
["3/0",null,"84 x 62",961,"N/A",1.38,200,215,5000,"Yes",1.213,16.56,167800,null,167800]
["4/0",58374199,"78 x 54",null,null,null,230,245]
[250,58089699,"78 x 54",null,null,null,250,270]
["350",null,"78 x 54",1287,"N/A",1.585,305,330,3000,"Yes",1.42,19.02,350000,null,350000]
["500",58089599,"78 x 54",1622,"N/A",1.765,370,400,2500,"Yes",1.53,21.18,500000,null,500000]
["600"]
["750",null,"84 x 62",2075,"N/A",1.955,455,490,2500,"Yes",1.725,23.46,750000,null,750000]
["1000",{"$nulls":5},525,565]
[1250]
[1500]
{"$rows_empty":8}
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","15kV 220 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-20C (-4F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46403+CU+3C+220NLEPR+tape+CPE+15KV+133.pdf"]
[null,null,"Product #","EFC CT3-13ET CPE Jkt"]
[null,null,"Spec #",46403]
["CATALOG SPEC EFC CT3 - 13ET CPE Jkt",{"$nulls":10},"CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Non Armored CPE Jacketed"]
["3/C, 15KV, 220 MILS EPR, 25% OVERLAP TAPE SHIELD, GW, CPE JACKET, CT RATED, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2]
[1]
["1/0",58404199,"96 x 63",2837,4,2.229,210,215,3000,"Yes",null,15.603000000000002,105600,918,358540]
["2/0"]
["3/0",58404299,"96 x 63",3813,3,2.488,270,280,2500,"Yes",null,17.416,167800,1008,556020]
["4/0",56025199,"96 x 55",4246,3,2.941,305,320,2000,"Yes",null,20.587,211600,1063,687420]
[250,{"$nulls":15},"56-12-32-99"]
["350",56378599,"96 x 63",6182,2,2.941,400,430,1500,"Yes",null,20.587,350000,1223,1116360]
["500",56123299,"96 x 63",8162,1,3.48,485,525,1000,"Yes",null,24.36,500000,1348,1583690]
["750"]
["1000"]
{"$rows_empty":12}
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","5kV 115 Mil EPR 133% CU Tape"]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. "]
[null,null,"Min Installation Temp","-20C (-4F)"]
[null,null,"URL Address","https://s3.amazonaws.com/swspec/MV/SPEC46203+CU+3C+115NLEPR+tape+CPE+5KV+133.pdf"]
[null,null,"Product #","EFC CT3-09ET CPE Jkt"]
[null,null,"Spec #",46203]
["CATALOG SPEC EFC CT3 - 09ET CPE Jkt",{"$nulls":10},"CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Non Armored CPE Jacketed"]
["3/C, 5KV, 115 MILS EPR, 25% OVERLAP TAPE SHIELD, GW, CPE JACKET, CT RATED, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str"]
["10 Str"]
["8"]
[6]
[4]
[2,55234599,"92 x 54",1573,6,1.551,160,165,5000,"Yes",0.623,10.857,66360,633,225320]
[1]
["1/0",null," "]
["2/0",55184899,"92 x 54",2657,4,1.938,235,245,3000,"Yes",0.743,13.565999999999999,133100,753,441040]
["3/0"]
["4/0",56103899,"84 x 54",3530,3,2.09,305,320,2000,"Yes",0.848,14.629999999999999,211600,858,687420]
[250]
["350",56045099,"92 x 54",5243,2,2.457,400,430,2000,"Yes",1.008,17.198999999999998,350000,1018,1116360]
["500",56123099,"96 x 62.5",7089,1,2.767,485,525,2000,"Yes",1.133,19.369,500000,1143,1583690]
["750",56044999,"96 x 62.5",9971,"1/0",3.185,585,635,1500,"Yes",1.32,22.295,750000,1330,2355600]
["1000"]
{"$rows_empty":8}
[null,null,"CU or AL","CU"]
[null,null,"Conductor count","3 / C WG"]
[null,null,"Voltage / Ins  level / shield","2kV XLP RHH/ RHW-2 "]
[null,null,"Armor","None"]
[null,null,"Jacket","CPE-PO"]
[null,null,"Max Sidewall pressure ",1000]
[null,null,"High Potential testing","N / A"]
[null,null,"Min Installation Temp","-20C (-4F)"]
[null,null,"URL Address","http://media.industrial.southwire.com/spec/spec45000/SPEC45451+CU+3C+XLPE+RHW+PVC+2000V+W3CUGW+VFD.pdf"]
[null,null,"Product #","3/C 2kV RHH/RHW CPE Jacketed TC"]
[null,null,"Spec #",45451]
["CATALOG SPEC 2 KV RHH/RHW CPE Jacketed TC VFD",{"$nulls":10},"CU 3 / C WG 2kV XLP RHH/ RHW-2  Non Armored CPE Jacketed"]
["3/C, 2kV XLP RHH/ RHW-2 GW, CPE JACKET, CT RATED, MV-105"]
["3/C     SIZE","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Duct 310.79 @ 105 C","Conduit in Air 310.75 @ 105 C","max length","CT Rated","Single O.D.","Min Bend Radius","Cmil (sgl)","Ext Shld Dia","Metal Area used for tensions"]
[]
["14 Str"]
["12 Str",56599999,"48x31.5",226,12,0.62,20,"N/A",5000,"Yes",0.207,4.34,6530,null,26120]
["10 Str",56598999,"48x31.5",296,10,0.677,30,"N/A",5000,"Yes",0.231,4.739000000000001,10380,null,41520]
["8",56600599,"50 x 34",410,10,0.817,55,"N/A",4000,"Yes",0.282,5.718999999999999,16510,null,59910]
[6,{"$nulls":5},75,"N/A"]
[4,56600299,"66 x 36",735,8,0.961,95,"N/A",4000,"Yes",0.364,6.726999999999999,41740,null,125220]
[2,56600199,"60 x 36",1058,6,1.084,130,"N/A",3000,"Yes",0.42,7.588000000000001,66360,null,225320]
[1,{"$nulls":5},145,"N/A"]
["1/0",56601599,"72 x 42",1592,6,1.347,170,"N/A",3000,"Yes",0.542,9.429,105600,null,358540]
["2/0",56600399,"72 x 42",1911,6,1.446,195,"N/A",3000,"Yes",0.588,10.122,133100,null,441040]
["3/0",{"$nulls":5},225,"N/A"]
["4/0",56664599,"72 x 42",2920,4,1.773,260,"N/A",2000,"Yes",0.693,12.411,211600,null,687420]
[250,{"$nulls":5},290,"N/A",null,null,null,0,250000,null,802620]
["350",56600499,"78 x 54",4578,3,2.124,350,"N/A",2000,"Yes",0.874,14.868,350000,null,1116360]
["500",56601699,"78 x 54",6187,2,2.396,430,"N/A",1500,"Yes",1,16.772,500000,null,1583690]
["750",56664499,"92 x 55",9224,"1",2.912,535,"N/A",1250,"Yes",1.211,20.384,750000,null,2355600]
["1000"]

{"sheet":"Conductor PC Comp","index":24,"n_rows":104,"n_cols":41,"rows_kept":104,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["11813",null,"M","C","V","A","J","R","Metal","CCC","Volt","Armor","Jacket","Size","Stock Number","reel size","Wt / MFT","GW size","Overall Diameter","Ampacity 1","Ampacity 2","max length","CT Rated","High pot testing","Max Sidewall Pressure","Min Inst Temp","Product#","URL","Short Circuit Factor","COF","# Conductors","Min Bend Radius","Header G","Header H","Shield Short Circuit Factor","No. of Conductors","Cmil (sgl)","Ext Ins Shld Dia (+10)","Metal Area used for tensions","Conductor","Desc"]
[11813,null,1,1,2,1,1,11211,"CU","1/C","600 XHHW","None","None","500",55701799,"66 x 42",1645,"N/A",0.923,430,700,4500,"Yes","N/A",1000,"- 40C (-40F)","XHHW/CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45001+CU+1C+XLPE-SIM+XHHW+none+600V+.pdf",0.0719,0.35,1,3.692,0,0,"N/A",1,500000,0,500000,"500","CU 1 / C 600V SIMpull XHHW ( XLP)"]
[null,null,1,1,1,1,1,11111,"CU","1/C","600 RHH","None","None","500",89010999,"66 x 42",1693,"N/A",0.983,430,700,4500,"Yes","N/A",1000,"- 40C (-40F)","RHH or RHW-2 / CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45003+CU+1C+XLPE+RHW+none+600V+.pdf",0.0719,0.35,1,3.932,0,0,"N/A",1,500000,0,500000,"500","CU 1 / C 600V RHH RHW USE (XLP) Non Armored Non Jacketed"]
["https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",null,1,1,2,1,2,11212,"CU","1/C","600 XHHW","None","PVC","500",89002299,"66 x 42",1763,"N/A",1.053,430,700,4000,"Yes","N/A",1000,"-10C (14F)","XHHW/PVC CT","https://s3.amazonaws.com/swspec/spec45000/SPEC45002+CU+1C+XLPE+XHHW+PVC+600V+.pdf",0.0719,0.35,1,5.265,0,0,"N/A",1,500000,0,500000,"500","CU 1 / C 600V XHHW ( XLP) Non Armored PVC Jacketed"]
[null,null,1,2,3,1,2,12312,"CU","3/C WG","600 THHN","None","PVC","500",44352399,"92 x 55",5906,"2 bare",2.22,380,430,2000,"Yes","N/A",500,"-10C (14F)","Type TC THHN","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf",0.0529,0.35,3,13.32,0,0,"N/A",3,500000,0,1566360,"500","CU 3 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
[null,null,1,3,3,1,2,13312,"CU","4/C WG","600 THHN","None","PVC","500",55251399,"92 x 55",7652,"2 bare",2.455,380,430,1500,"Yes","N/A",500,"-10C (14F)","Type TC THHN","http://media.industrial.southwire.com/spec/spec45000/SPEC45251+CU+3C+PVC-nylon+THHN+PVC-SIM+600V+W1CUGW.pdf",0.0529,0.35,4,14.73,0,0,"N/A",4,500000,0,2066360,"500","CU 4 / C WG 600V THHN THWN Non Armored PVC Jacketed"]
["Size",null,1,2,2,1,2,12212,"CU","3/C WG","600 XHHW","None","PVC","500"," 48-07-23-99","92 x 55",5755,"2 bare",2.214,380,430,2000,"Yes","N/A",500,"-10C (14F)","Type TC XHHW","http://media.industrial.southwire.com/spec/spec45000/SPEC45252+CU+3C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf",0.0719,0.35,3,13.283999999999999,0,0,"N/A",3,500000,0,1566360,"500","CU 3 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
["CU","AL",1,3,2,1,2,13212,"CU","4/C WG","600 XHHW","None","PVC","500",55446999,"92 x 55",7562,"2 bare",2.448,380,430,1500,"Yes","N/A",500,"-10C (14F)","Type TC XHHW","http://media.industrial.southwire.com/spec/spec45000/SPEC45258+CU+4C+XLPE+XHHW+PVC-SIM+600V+W1CUGW.pdf",0.0719,0.35,4,14.687999999999999,0,0,"N/A",4,500000,0,2066360,"500","CU 4 / C WG 600V XHHW / XLP Non Armored PVC Jacketed"]
[16,18,1,2,2,1,4,12214,"CU","3/C WG","600 XHHW","None","CPE-PO","500",89071099,"78 x 54",5853,"2 bare",2.214,380,430,1500,"Yes","N/A",500,"- 40C (-40F)","Type TC XHHW CPE","http://media.industrial.southwire.com/spec/spec45000/SPEC45255+CU+3C+EPR+XHHW+CPE+600V+W1CUGW.pdf",0.0719,0.5,3,13.283999999999999,0,0,"N/A",3,500000,0,1566360,"500","CU 3 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[0,0,1,3,2,1,5,13215,"CU","4/C WG","600 XHHW","None","CPE-PO","500","55-03-91-99","92 x 55",7586,"2 bare",2.448,380,430,1500,"Yes","N/A",500,"- 40C (-40F)","Type TC XHHW/CPE","http://media.industrial.southwire.com/spec/spec45000/SPEC45262+CU+4C+EPR+XHHW+CPE+600V+W1CUGW.pdf",0.0719,0.5,4,14.687999999999999,0,0,"N/A",4,500000,0,2066360,"500","CU 4 / C WG 600V XHHW / XLP Non Armored CPE-CPO Jacketed"]
[null,null,1,1,5,1,3,11513,"CU","1/C","2.4 KV","None","SIMpull PVC","500","60-73-09-99","78 x 54",2088,"N/A",1.357,470,505,4000,"Yes ","N/A",1000,"-10C (14F)","EFC 09ENS/SIMpull PVC","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf",0.0678,0.2,1,10.856,0,0,"N/A",1,500000,0,500000,"500","CU 1 / C 2.4 kV Non Shielded Non Armored SIMpull-PVC Jacketed"]
[null,null,1,1,5,1,8,11518,"CU","1/C","2.4 KV","None","SOLONON","500",61117899,"78 x 54",2101,"N/A",1.357,470,505,4000,"YES","N/A",1000,"-40C (-40F)","EFC 09ENS/LSZH","https://s3.amazonaws.com/swspec/MV/SPEC46002+CU+1C+EPR+none+PVC-SIM+2.4KV+.pdf",0.0678,0.2,1,10.856,0,0,"N/A",1,500000,0,500000,"500","CU 1 / C 2.4 kV Non Shielded Non Armored SOLONON XPL Jacketed"]
["Item",null,1,1,6,1,3,11613,"CU","1/C","5KV","None","SIMpull PVC","500","95-50-54-99","78 x 54",2067,"N/A",1.3,470,505,3000,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-09ET SIMpull ","https://s3.amazonaws.com/swspec/MV/SPEC46102+CU+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf",0.0678,0.2,1,15.600000000000001,0,0,"N/A",1,500000,1143,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
["CU","AL",1,1,7,1,3,11713,"CU","1/C","15KV 175","None","SIMpull PVC","500",95382899,"78 x 54",2201,"N/A",1.415,465,500,3500,"No","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC 11ET SIMpull ","https://s3.amazonaws.com/swspec/MV/SPEC46301+CU+1C+175NLEPR+tape+PVC-SIM+15KV+100.pdf",0.0678,0.2,1,16.98,0,0,"N/A",1,500000,1258,500000,"500","CU 1 / C 15kV 175 Mil EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
[11813,21813,1,1,8,1,3,11813,"CU","1/C","15KV 220","None","SIMpull PVC","500","95-60-45-99","72 x 42",2317,"N/A",1.505,465,500,3000,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-13ET SIMpull PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46302+CU+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",0.0678,0.2,1,18.06,0,0,"N/A",1,500000,1348,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[null,"21813",1,1,6,1,4,11614,"CU","1/C","5KV","None","CPE-PO","500","55-05-21-99","78 x 54",2137,"N/A",1.39,470,505,4000,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","CT1-09ET-C","https://s3.amazonaws.com/swspec/MV/SPEC46103+CU+1C+115NLEPR+tape+CPE+5KV+133.pdf",0.0678,0.5,1,16.68,0,0,"N/A",1,500000,1143,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
[null,null,1,1,8,1,4,11814,"CU","1/C","15KV 220","None","CPE-PO","500","55-05-08-99","78 x 42",2388,"N/A",1.567,465,500,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-20C (-4F)","CT1-13ET-C","https://s3.amazonaws.com/swspec/MV/SPEC46304+CU+1C+220NLEPR+tape+CPE+15KV+133.pdf",0.0678,0.5,1,18.804,0,0,"N/A",1,500000,1348,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored CPE-PO Jacketed"]
[null,null,1,1,6,1,6,11616,"CU","1/C","5KV","None","Solo PO","500","55-07-83-99","78 x 42",2137,"N/A",1.39,470,505,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","CT1-09ET-S","https://s3.amazonaws.com/swspec/MV/SPEC46104+CU+1C+115NLEPR+tape+LSZH+5KV+133.pdf",0.0678,0.35,1,16.68,0,0,"N/A",1,500000,1200,500000,"500","CU 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
[null,null,1,1,8,1,6,11816,"CU","1/C","15KV 220","None","Solo PO","500","55-07-89-99","78 x 42",2355,"N/A",1.567,465,500,3000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","CT1-13ET-S","https://s3.amazonaws.com/swspec/MV/SPEC46305+CU+1C+220NLEPR+tape+LSZH+15KV+133.pdf",0.0678,0.35,1,18.804,0,0,"N/A",1,500000,1410,500000,"500","CU 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SOLONON-PO Jacketed"]
[null,null,1,1,9,1,3,11913,"CU","1/C","25KV 320 ","None","SIMpull PVC","500",64462399,0,2582,"N/A",1.715,465,500,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 75kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)",0,"http://media.industrial.southwire.com/spec/spec46000/SPEC46502+CU+1C+320NLEPR+tape+PVC-SIM+25KV+133.pdf",0.0678,0.2,1,20.580000000000002,0,0,"N/A",1,500000,1.545,500000,"500","CU 1 / C 25kV 320 MIL EPR 133% CU Tape Non Armored SIMpull-PVC Jacketed"]
[null,null,1,1,11,1,3,111113,"CU","1/C","35kV 345 ","None","SIMpull PVC","500",55588899,"78 x 54",2761,"N/A",1.813,465,500,2500,"No","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1 19ET SIMpull PVC JKT","https://s3.amazonaws.com/swspec/MV/SPEC46701+CU+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf",0.0678,0.2,1,21.756,0,0,"N/A",1,500000,1593,500000,"500","CU 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacketed"]
[null,null,1,1,12,1,3,111213,"CU","1/C","35KV 420","None","SIMpull PVC","500","89-00-68-99","84 x 62",3011,"N/A",1.965,465,500,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT1-21ET SIMpull PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46702+CU+1C+420NLEPR+tape+PVC-SIM+35KV+133.pdf",0.0678,0.2,1,23.580000000000002,0,0,"N/A",1,500000,1745,500000,"500","CU 1 / C 35kV 420 Mil EPR 133% CU Tape Non Armored SIMpul- PVC Jacketed"]
[null,null,1,2,6,1,2,12612,"CU","3/C WG","5KV","None","PVC","500",95839799,"104 x 57",7103,1,2.78,485,525,2000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT3-09ET PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46202+CU+3C+115NLEPR+tape+PVC+5KV+133.pdf",0.0678,0.2,3,19.459999999999997,0,0,"N/A",3,500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Non Armored  PVC Jacketed"]
[null,null,1,2,8,1,2,12812,"CU","3/C WG","15KV 220","None","PVC","500",95833099,"96 x 63",8056,1,3.223,485,525,1000,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","EFC CT3-13ET PVC Jkt","https://s3.amazonaws.com/swspec/MV/SPEC46402+CU+3C+220NLEPR+tape+PVC+15KV+133.pdf",0.0678,0.2,3,22.561,0,0,"N/A",3,500000,1348,1583690,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Non Armored PVC Jacketed"]
[null,null,1,2,5,1,2,12512,"CU","3/C WG","2.4 KV","None","PVC","500","60-03-87-99","92 x 55",6444,1,2.536,460,475,1750,"Yes","N/A",1000,"-10C (14F)","EFC CT3-09ENS PVC Jkt",0,0.0678,0.2,3,17.752,0,0,"N/A",3,500000,0,1500000,"500","CU 3 / C WG 2.4 kV Non Shielded Non Armored PVC Jacketed"]
[null,null,1,2,2,3,2,12232,"CU","3/C WG","600 XHHW","AIA","PVC","500","38-06-18-99","92 x 55",6104,2,2.462,0,487,2000,"Yes","N/A",500,"-10C (14F)","AL01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45301+CU+3C+XLPE+XHHW+AIA+PVC+600V+W1CUGW.pdf",0.0719,0.35,3,17.234,0,0,"N/A",3,500000,0,1566360,"500","CU 3 / C WG 600V AIA Armored PVC Jacketed"]
[null,null,1,2,5,3,2,12532,"CU","3/C WG","2.4 KV","AIA","PVC","500","89-06-45-99","96 x 63",6556,1,2.687,530,485,2100,"Yes","N/A",500,"-10C (14F)","AL09ENS","https://s3.amazonaws.com/swspec/MV/SPEC46026+CU+3C+115EPR+none+AIA+PVC+2.4KV+100.pdf",0.0678,0.35,3,18.808999999999997,0,0,"N/A",3,500000,0,1583690,"500","CU 3 / C WG 2.4 kV Non Shielded AIA Armored PVC Jacketed"]
[null,null,1,2,6,3,2,12632,"CU","3/C WG","5 KV","AIA","PVC","500",55668899,"96 x 63",7262,1,2.957,590,600,1600,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",500,"-10C (14F)","AL09ET","https://s3.amazonaws.com/swspec/MV/SPEC46254+CU+3C+115NLEPR+tape+AIA+PVC+5KV+133.pdf",0.0678,0.35,3,20.698999999999998,0,0,"N/A",3,500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
[null,null,1,2,8,3,2,12832,"CU","3/C WG","15KV 220","AIA","PVC","500","40-91-69-99","108 x 71",8299,1,3.42,590,600,1600,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",500,"-10C (14F)","AL13ET","https://s3.amazonaws.com/swspec/MV/SPEC46453+CU+3C+220NLEPR+tape+AIA+PVC+15KV+133.pdf",0.0678,0.35,3,23.939999999999998,0,0,"N/A",3,500000,1348,1583690,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape AIA Armored PVC Jacketed"]
[null,null,1,3,2,4,2,13242,"CU","4/C WG","600 XHHW","Armor-X","PVC","500",89053699,"96 x 55",7721,"1 x #2",2.82,0,344,1500,"YES","N/A",1000,"-40C (-40F)","HLX01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45352+CU+4C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf",0.0719,0.35,4,19.74,0,0,"N/A",4,500000,0,2066360,"500"," CU 4 / C WG Armor-X (CCW) Armored PVC Jacketed"]
[null,null,1,2,2,4,2,12242,"CU","3/C WG","600 XHHW","Armor-X","PVC","500",89052299,"84 x 54",6001,"3 x #6",2.58,0,430,1500,"YES","N/A",1000,"-40C (-40F)","HLX01XXH","http://media.industrial.southwire.com/spec/spec45000/SPEC45351+CU+3C+XLPE+XHHW+ARMOR-X+PVC+600V+W3CUGW.pdf",0.0719,0.35,3,18.060000000000002,0,0,"N/A",3,500000,0,1578720,"500","CU 3 / C WG 600V Armor-X (CCW) Armored PVC Jacketed"]
[null,null,1,2,5,4,2,12542,"CU","3/C WG","2.4 KV","Armor-X","PVC","500",89062199,"96 x 55",6571,"3x4",2.82,530,485,1500,"YES","N/A",1000,"-40C (-40F)","XAL07ENS","https://s3.amazonaws.com/swspec/MV/SPEC46027+CU+3C+90EPR+none+ARMOR-X+PVC+2.4KV+100.pdf",0.0678,0.35,3,19.74,0,0,"N/A",3,500000,0,1500000,"500","CU 3 / C WG 2.4 kV Non Shielded Armor-X (CCW) Armored PVC Jacketed"]
[null,null,1,2,6,4,2,12642,"CU","3/C WG","5KV","Armor-X","PVC","500",89064399,"96 x 55",7363,1,3.13,570,545,1300,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","HLX09ET","https://s3.amazonaws.com/swspec/MV/SPEC46255+CU+3C+115NLEPR+tape+ARMOR-X+PVC+5KV+133.pdf",0.0678,0.35,3,21.91,0,0,"N/A",3,500000,1143,1583690,"500","CU 3 / C WG 5kV 115 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
[null,null,1,2,8,4,2,12842,"CU","3/C WG","15KV 220","Armor-X","PVC","500",89066999,"108 x 71  ",8674,1,3.71,590,600,1300,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-40C (-40F)","HLX13ET","https://s3.amazonaws.com/swspec/MV/SPEC46454+CU+3C+220NLEPR+tape+ARMOR-X+PVC+15KV+133.pdf",0.0678,0.35,3,25.97,0,0,"N/A",3,500000,1348,1500000,"500","CU 3 / C WG 15kV 220 Mil EPR 133% CU Tape Armor-X (CCW) Armored PVC Jacketed"]
[null,null,1,2,4,5,2,12452,"CU","3/C WG","1KV","Tech 90","PVC","500",56196199,"84 x 54",6802,3,2.777,0,0,1500,0,"N/A",500,"-40 C (-40 F)","3/C 1kV Tech 90","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheetT90",0.0678,0.35,3,41.655,0,0,"N/A",3,500000,0,1552620,"500","CU 3 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[null,null,1,3,4,5,2,13452,"CU","4/C WG","1KV","Tech 90","PVC","500",56196299,"96 x 55",8602,3,3.024,0,0,1000,0,"N/A",500,"-40C (-40F)","4/C 1kV Tech 90","http://www.southwire.com/ProductCatalog/XTEInterfaceServlet?contentKey=prodcatsheet329",0.0678,0.35,4,45.36,0,0,"N/A",4,500000,0,2052620,"500","CU 4 / C WG 1kV Non Shielded Tech 90 Armored PVC Jacketed"]
[null,null,2,1,2,1,1,21211,"AL","1 / C","600V XHHW ( XLP)","None","None","750",56038199,"84 x 42",851,"N/A",1.071,385,435,3000,"Yes","N/A",500,"- 40C (-40F)","AL XHHW/CT","http://media.industrial.southwire.com/spec/spec45000/SPEC45007+AL+1C+XLPE+XHHW+none+600V+.pdf",0.047,0.35,1,5.3549999999999995,0,0,"N/A",1,750000,0,750000,"750","AL 1 / C 600V XHHW ( XLP) Non Armored Non Jacketed"]
[null,null,2,1,6,1,3,21613,"AL","1 / C","5kV 115 Mil EPR 133% CU Tape","None","SIMpull PVC","750",56017999,"72 x 42",1353,"N/A",1.483,470,505,2500,"YES","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 28kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-09ET","https ://s3.amazonaws.com/swspec/MV/SPEC46110+AL+1C+115NLEPR+tape+PVC-SIM+5KV+133.pdf",0.0443,0.35,1,17.796,0,0,"N/A",1,750000,1220,750000,"750","AL 1 / C 5kV 115 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[null,null,2,1,8,1,3,21813,"AL","1 / C","15kV 220 Mil EPR 133% CU Tape","None","SIMpull PVC","750",56011899,"78 x 54",1717,"N/A",1.744,455,490,2500,"Yes ","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 56kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-13ET","https://s3.amazonaws.com/swspec/MV/SPEC46311+AL+1C+220NLEPR+tape+PVC-SIM+15KV+133.pdf",0.0443,0.35,1,20.928,0,0,"N/A",1,750000,1470,750000,"750","AL 1 / C 15kV 220 Mil EPR 133% CU Tape Non Armored SIMpull-PVC Jacket"]
[null,null,2,1,11,1,3,211113,"AL","1 / C","35kV 345 MIL EPR 100% CU Tape","None","SIMpull PVC","750",0,"84 x 62",2075,"N/A",1.955,455,490,2500,"Yes","System Voltage (kV rms) (phase -phase).  Acceptance test voltage is 100kV -dc (cond-grd), normally for 15 minutes. ",1000,"-10C (14F)","CT1A-19ET","https://s3.amazonaws.com/swspec/MV/SPEC46709+AL+1C+345NLEPR+tape+PVC-SIM+35KV+100.pdf",0.0443,0.35,1,23.46,0,0,"N/A",1,750000,0,750000,"750","AL 1 / C 35kV 345 MIL EPR 100% CU Tape Non Armored SIMpull-PVC Jacket"]
[null,null,1,2,8,1,4,12814,"CU","3/C WG","15kV 220 Mil EPR 133% CU Tape","None","CPE-PO",{"$nulls":15}," "]
[null,null,1,2,6,1,4,12614,"CU","3/C WG","5kV 115 Mil EPR 133% CU Tape","None","CPE-PO",{"$nulls":15}," "]
[null,null,1,2,13,1,4,121314,"CU","3/C WG","2kV XLP  RHH / RHW-2 ","None","CPE-PO",{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,0,0,0,0,0,0,{"$nulls":15}," "]
[null,null,0,0,0,0,0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34]
{"$rows_empty":8}
["CU","AL","CU"]
[11211,21211,11211]
[11613,21613,11613]
[11813,21813,11813]
[111113,211113,111113]

{"sheet":"Power Cable Comp Calc","index":25,"n_rows":79,"n_cols":37,"rows_kept":79,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,null,"SIMpull","Non-SIMpull","AL SIMpull"]
[null,null,"500","500","750",{"$nulls":7},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
["Allow Stress (lbs/cmil)","S",0.008,0.008,0.006,{"$nulls":5},"Length","L",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
["Area of Conductor (cmil)","A",0,0,0,{"$nulls":5},"Straight Section Radians","q",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
["Number of Conductors","N",0,0,0,{"$nulls":5},"Bend Section Radians","f",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
["Wt Corr. Fct. ","w",1.4,1.4,1.4,{"$nulls":5},"Bend Radius (ft)","R",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
["Coefficient of Friction","m",0.2,0.35,0.2,{"$nulls":6},"AL R",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
["Total Cable Wt. (Lbs/ft)","W",0,0,0,{"$nulls":6},"SIMpull",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
["Natural Logarithm base","e",2.718281828459045,2.718281828459045,2.718281828459045,{"$nulls":6},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
["Tension On Each Conductor (lbs)","TC",0,0,0,{"$nulls":5},{"$error":"#VALUE!"},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
["Max allowable tension on device (lbs)","Tcable",0,0,0,{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Conduit Inner Diameter ","D",0.622,0.622,0.622,{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Outter Diameter of Cable","d",1.505,1.505,1.744,{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Conductor short circuit factor","Fc",0.0678,0.0678,0.0443,{"$nulls":7},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"t",0.0333,0.0333,0.0333]
[null,"wm2",0.07839999999999998,0.24009999999999992,0.07839999999999998,{"$nulls":6},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]
[]
[null,"Area of Conductor (cmil) for Short circuit calc",500000,500000,750000]
[null,"Short Circuit Calc",185770,185770,182071,{"$nulls":6},"Non-SIMpull",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[{"$nulls":11},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Maximum Pulling Force (lb.)",0,0,0,{"$nulls":6},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Max Sidewall Pres. (lb.)",0,500,0,{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[null,"Isc",185770.85565505372,185770.85565505372,182071.87844068318]
[null,"Metal Area used for tensions",0,0,0]
[]
[]
[]
[]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Total Ouside Diameter of Cable",0,0,0,{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 1 in2",0,0,0,{"$nulls":7},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 2 in2",0,0,0]
[null,"Cable 3 in2",0,0,0,{"$nulls":6},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Cable Total in2",0,0,0]
[null,"Minimum Recommended Conduit Size",0.5,0.5,0.5]
[null,"Conduit Inner Diameter",0.622,0.622,{"$nulls":8},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[{"$nulls":11},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Ground Wire",0,0,0,{"$nulls":6},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Fill Rate",0,0,{"$error":"#DIV/0!"},{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,null,"0.5\" EMT (0% fill)","0.5\" EMT (0% fill)",{"$error":"#DIV/0!"},{"$nulls":7},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 1 wt.",0,0,0,{"$nulls":7},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 2 wt.",0,0,0]
[null,"Cable 3 wt.",0,0,0,{"$nulls":6},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Total wt.",0,0,0]
[]
[{"$nulls":12},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[null,"Maxis Grips Index",{"$nulls":9},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Maxis Grip Size",{"$nulls":9},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,"Min Conduit Size",{"$nulls":10},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]
[null,null,"In2"]
[null,null,"Cable 1","Cable 2",null,"Total"]
[null,null,0,0,0,0,{"$nulls":5},"AL SIMpull",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[{"$nulls":11},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
[{"$nulls":4},"Index","Conduit I.D.",{"$nulls":5},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
[{"$nulls":4},2,0.622,{"$nulls":6},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]
[]
[]
[{"$nulls":12},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25]
[{"$nulls":11},"Tension In","","","","","","","","","","","","","","","","","","","","","","","","",""]
[{"$nulls":11},"Tension Out","","","","","","","","","","","","","","","","","","","","","","","","",""]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","","","","","","","","",""]

{"sheet":"Reels","index":26,"n_rows":29,"n_cols":42,"rows_kept":29,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[null,0.065,null,0.04]
[null,"Reel","Flange","Traverse","Drum","Max Width","Capacity (lb)","600V","Power Cable",null,null,"Tare Wt.","Index","(Dia X Width)",null,"Length","total wires","# of  wires","Sets","Calc OD","Clearance","Volume Range Ref","Volume","Wire wt","Single Reel Ref","Single Reel","Bend Radius","Gross wt (wire wt plus tare wt)","Stacked Volume","Stacked Wire wt","Stacked Reel Ref","Stacked Reel","L1","L2","S1","S2",1,2,3,4,5,6]
[null,"N7",30,17,17,20,950,6312.1822073722215,6312.1822073722215,null,null,30,1,"N7 (30\" X 20\")","Power Cable",0,0,0,1,null,null,null,0,0,0,"N7",0,30,0,0,0,"N7 (30\" X 20\")",0,0,0,0,0,0,0,0,0,0]
[null,"N15",32,22,14,25,1250,11589.099051325196,11589.099051325196,null,null,50,2,"N15 (32\" X 25\")"]
[null,"C17",34,24,16,27.5,2500,13617.643020666988,13617.643020666988,null,null,62.4,3,"C17 (34\" X 27.5\")","600V",0,0,0,1,null,null,null,0,0,0,"C17",0,62.4,0,0,0,"C17 (34\" X 27.5\")",0,0,0,0,0,0,0,0,0,0]
[null,"N19",34,26.5,15,29.5,1400,15681.35209321747,15681.35209321747,null,null,92,4,"N19 (34\" X 29.5\")"]
[null,"N25F",40,24,17,27.5,2500,20079.300949859942,20079.300949859942,null,null,73,5,"N25F (40\" X 27\")"]
[null,"N29C",42,26,18,29.5,3000,23872.404627773565,23872.404627773565,null,null,93.66,6,"N29C (42\" X 31\")"]
[null,"C38A",48,28,24,32,4800,30218.160407516156,30218.160407516156,null,null,96,7,"C38A (48\" X 34\")"]
[null,"N48",50,30,21,34,3500,39466.25771072177,39466.25771072177,null,null,121.65,8,"N48 (50\" X 34\")"]
[null,"A62R",60,28,28,34,6800,49766.848871458926,49766.848871458926,null,null,164.75,9,"A62R (60\" X 34\")"]
[null,"R16",66,32,32,36,6000,66926.43906039269,66926.43906039269,null,null,282.43,10,"R16 (66\" X 36\")"]
[null,"N86",66,36,36,42,7500,67601.62512695396,67601.62512695396,null,null,198,11,"N86 (66\" X 42\")"]
[null,"R23",78,36,48,42,8000,80454.54920370651,80454.54920370651,null,null,303,12,"R23 (78\" X 42\")"]
[null,"R20",72,36,36,42,8000,87416.82117888604,87416.82117888604,null,null,397.45,13,"R20 (72\" X 42\")"]
[null,"R24",84,36,48,42,10000,103715.8663081485,103715.8663081485,null,null,353,14,"R24 (84\" X 42\")"]
[null,"R22",78,36,36,42,8000,108955.07775707312,108955.07775707312,null,null,536.39,15,"R22 (78\" X 42\")"]
[null,"R47",84,56,56,61.5,6000,124742.52080588376,124742.52080588376,null,null,710,16,"R47 (84\" X 61.5\")"]
[null,"R25",84,48,48,54,10000,138287.821744198,138287.821744198,null,null,591,17,"R25 (84\" X 54\")"]
[null,"R32",78,48,36,54,10000,145273.4370094308,145273.4370094308,null,null,803,18,"R32 (78\" X 54\")"]
[null,"R26",84,56,48,62,10000,161335.79203489766,161335.79203489766,null,null,676,19,"R26 (84\" X 62\")"]
[null,"R27",92,48,48,54.5,12500,183215.029539883,183215.029539883,null,null,952,20,"R27 (92\" X 54.5\")"]
[null,"R28",96,48,48,54.5,12500,207210.2427943965,207210.2427943965,null,null,847,21,"R28 (96\" X 54.5\")"]
[null,"R30",96,56,56,62.5,12500,205152.01203111533,205152.01203111533,null,null,709,22,"R30 (96\" X 62.5\")"]
[null,"R29",96,56,48,62.5,15000,241745.28326012925,241745.28326012925,null,null,877,23,"R29 (96\" X 62.5\")"]
[null,"R40",96,56,48,65,20000,241745.28326012925,241745.28326012925,null,null,1082,24,"R40 (96\" X 65\")"]
[null,"R34",104,50,50,56.5,15000,261327.9813495028,261327.9813495028,null,null,1159,25,"R34 (104\" X 56.5\")"]
[null,"R31",108,64,60,70.5,15000,315285.69471465744,315285.69471465744,null,null,1237,26,"R31 (108\" X 70.5\")"]
[null,"R38",108,64,60,73,20000,315285.69471465744,315285.69471465744,null,null,1195,27,"R38 (108\" X 73\")"]

{"sheet":"BEM Reels","index":27,"n_rows":39,"n_cols":13,"rows_kept":39,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["Reel","Flange","Traverse","Drum","Max Width","Wt. Capacity (lb)","600V","Power Cable",null,null,"Tare Wt.","Index","(Dia X Width)"]
["N7",30,17,17,20,950,6312.1822073722215,6312.1822073722215,null,null,30,1,"N7 (30\" X 20\")"]
["N15",32,22,14,25,1250,11589.099051325196,11589.099051325196,null,null,50,2,"N15 (32\" X 25\")"]
["C17",34,24,16,27.5,2500,13617.643020666988,13617.643020666988,null,null,62.4,3,"C17 (34\" X 27.5\")"]
["N19",34,26.5,15,29.5,1400,15681.35209321747,15681.35209321747,null,null,92,4,"N19 (34\" X 29.5\")"]
["N25F",40,24,17,27.5,2500,20079.300949859942,20079.300949859942,null,null,73,5,"N25F (40\" X 27\")"]
["N29C",42,26,18,29.5,3000,23872.404627773565,23872.404627773565,null,null,93.66,6,"N29C (42\" X 31\")"]
["C38A",48,28,24,32,4800,30218.160407516156,30218.160407516156,null,null,96,7,"C38A (48\" X 34\")"]
["N48",50,30,21,34,3500,39466.25771072177,39466.25771072177,null,null,121.65,8,"N48 (50\" X 34\")"]
["A62R",60,28,28,34,6800,49766.848871458926,49766.848871458926,null,null,164.75,9,"A62R (60\" X 34\")"]
["R16",66,32,32,36,6000,66926.43906039269,66926.43906039269,null,null,282.43,10,"R16 (66\" X 36\")"]
[]
["Additional Reels used in Canada"]
["N11, N29, N34, N62, N7P, R19, R20"]
[]
["Reels used for:"]
["Configurator / David Knerr 2-3-16, BEM and the Cable Pull Calc / Allen Hooper 2-3-16, Logistics / Dist Centers / Aaron Asher 2-3-16"]
[]
[]
["Power Cable Reels"]
["N86",66,36,36,42,7500,67601.62512695396,67601.62512695396,null,null,198,11,"N86 (66\" X 42\")"]
["R23",78,36,48,42,8000,80454.54920370651,80454.54920370651,null,null,303,12,"R23 (78\" X 42\")"]
["R20",72,36,36,42,8000,87416.82117888604,87416.82117888604,null,null,397.45,13,"R20 (72\" X 42\")"]
["R24",84,36,48,42,10000,103715.8663081485,103715.8663081485,null,null,353,14,"R24 (84\" X 42\")"]
["R22",78,36,36,42,8000,108955.07775707312,108955.07775707312,null,null,536.39,15,"R22 (78\" X 42\")"]
["R47",84,56,56,61.5,6000,124742.52080588376,124742.52080588376,null,null,710,16,"R47 (84\" X 61.5\")"]
["R25",84,48,48,54,10000,138287.821744198,138287.821744198,null,null,591,17,"R25 (84\" X 54\")"]
["R32",78,48,36,54,10000,145273.4370094308,145273.4370094308,null,null,803,18,"R32 (78\" X 54\")"]
["R26",84,56,48,62,10000,161335.79203489766,161335.79203489766,null,null,676,19,"R26 (84\" X 62\")"]
["R27",92,48,48,54.5,12500,183215.029539883,183215.029539883,null,null,952,20,"R27 (92\" X 54.5\")"]
["R28",96,48,48,54.5,12500,207210.2427943965,207210.2427943965,null,null,847,21,"R28 (96\" X 54.5\")"]
["R30",96,56,56,62.5,12500,205152.01203111533,205152.01203111533,null,null,709,22,"R30 (96\" X 62.5\")"]
["R29",96,56,48,62.5,15000,241745.28326012925,241745.28326012925,null,null,877,23,"R29 (96\" X 62.5\")"]
["R40",96,56,48,65,20000,241745.28326012925,241745.28326012925,null,null,1082,24,"R40 (96\" X 65\")"]
["R34",104,50,50,56.5,15000,261327.9813495028,261327.9813495028,null,null,1159,25,"R34 (104\" X 56.5\")"]
["R31",108,64,60,70.5,15000,315285.69471465744,315285.69471465744,null,null,1237,26,"R31 (108\" X 70.5\")"]
["R38",108,64,60,73,20000,315285.69471465744,315285.69471465744,null,null,1195,27,"R38 (108\" X 73\")"]
[]
["Reels used for Cable Pull Calc / Allen Hooper 2-3-16"]

{"sheet":"Products","index":28,"n_rows":22,"n_cols":18,"rows_kept":22,"cut":false,"hidden":true,"merged":[[1,15,1,17],[1,9,1,11],[1,0,1,2],[1,3,1,5],[1,6,1,8],[1,12,1,14]],"flags":["formulas_cached_only"]}
[]
["SIMpull CU THHN",null,null,"SIMpull AL THHN",null,null,"SIMpull CU XHHW",null,null,"AL XHHW",null,null,"CU USE",null,null,"AL USE"]
[1,"(in)","Weight",2,"(in)","(lb/1000ft)",3,"(in)","Weight",4,"(in)","(lb/1000ft)",5,"(in)","(lb/1000ft)",6,"(in)","(lb/1000ft)"]
["CUT","Diameter","(lb/1000ft)","ALT","Diameter","Weight","CUX","Diameter","(lb/1000ft)","ALX","Diameter","Weight","CUU","Diameter","Weight","ALU","Diameter","Weight"]
[6,0.249,95.0172,6,0.239,38.298,6,0.267,100,6,0.262,42,6,0.297,107,6,0.292,49]
[4,0.318,152.3074,4,0.305,61.9425,4,0.314,150,4,0.306,58,4,0.344,157,4,0.336,65]
[2,0.378,234.2434,2,0.36,90.509,2,0.37,231,2,0.361,86,2,0.4,240,2,0.391,94]
[1,0.435,299.4499,1,0.413,116.5709,1,0.434,292,1,0.412,110,1,0.484,309,1,0.462,126]
["1/0",0.474,371.5426,"1/0",0.45,141.41,"1/0",0.473,363,"1/0",0.449,134,"1/0",0.523,381,"1/0",0.499,151]
["2/0",0.518,461.6961,"2/0",0.49,171.92,"2/0",0.517,452,"2/0",0.489,163,"2/0",0.567,472,"2/0",0.539,182]
["3/0",0.568,575.1206,"3/0",0.537,210.09,"3/0",0.567,565,"3/0",0.536,200,"3/0",0.617,586,"3/0",0.586,221]
["4/0",0.624,717.5497,"4/0",0.589,257.52,"4/0",0.623,706,"4/0",0.588,247,"4/0",0.673,729,"4/0",0.638,269]
["250",0.694,850.8518,"250",0.656,310.66,250,0.691,835,250,0.653,296,250,0.751,867,250,0.713,326]
["300",0.747,1012.1303,"300",0.706,364.62,"300",0.744,995,"300",0.703,349,"300",0.804,1029,"300",0.763,381]
["350",0.797,1173.8844,"350",0.752,418.13,"350",0.794,1155,"350",0.749,401,"350",0.854,1191,"350",0.809,435]
["400",0.842,1333.9942,"400",0.795,471.24,"400",0.839,1314,"400",0.792,453,"400",0.899,1352,"400",0.852,489]
["500",0.926,1654.7757,"500",0.872,576.41,"500",0.923,1632,"500",0.869,556,"500",0.983,1674,"500",0.929,595]
["600",1.024,1986.3868,"600",0.971,699.68,"600",1.029,1966,"600",0.976,679,"600",1.089,2012,"-"]
["700",1.093,2304.7838,"700",1.035,804.36,"-",null,0,"-",null,null,"-",null,null,"-"]
["750",1.126,2464.08,"750",1.066,856.58,"750",1.131,2283,"750",1.071,833,"750",1.191,2492,"750",1.131,881]
["-",null,null,"900",1.157,1013.06,"-",null,0,"900",1.162,987,"-",null,null,"-"]
["1000",1.275,3256.530402,"1000",1.218,1117.55,"1000",1.28,3231,"1000",1.223,1090,"1000",1.34,3289,"1000",1.283,1145]

{"sheet":"Reverse","index":29,"n_rows":46,"n_cols":21,"rows_kept":46,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,0,"Wire pull / Segment","Angle    (Slope)","Wire is being pulled …","Segment Length ft.","Bend Type","Up, Down, N/A","Degree of elbow","Radius (in.)",null,null,0,"Wire pull / Segment","Angle    (Slope)","Wire is being pulled …","Segment Length ft.","Bend Type","Up, Down, N/A","Degree of elbow","Radius (in.)"]
[1,"",1,1,4,0,1,4,1,1,null,1,"",1,1,4,0,1,4,1,1]
[2,"",2,1,4,0,1,4,1,1,null,2,"",2,1,4,0,1,4,1,1]
[3,"",3,1,4,0,1,4,1,1,null,3,"",3,1,4,0,1,4,1,1]
[4,"",4,1,4,0,1,4,1,1,null,4,"",4,1,4,0,1,4,1,1]
[5,"",5,1,4,0,1,4,1,1,null,5,"",5,1,4,0,1,4,1,1]
[6,"",6,1,4,0,1,4,1,1,null,6,"",6,1,4,0,1,4,1,1]
[7,"",7,1,4,0,1,4,1,1,null,7,"",7,1,4,0,1,4,1,1]
[8,"",8,1,4,0,1,4,1,1,null,8,"",8,1,4,0,1,4,1,1]
[9,"",9,1,4,0,1,4,1,1,null,9,"",9,1,4,0,1,4,1,1]
[10,"",10,1,4,0,1,4,1,1,null,10,"",10,1,4,0,1,4,1,1]
[11,"",11,1,4,0,1,4,1,1,null,11,"",11,1,4,0,1,4,1,1]
[12,"",12,1,4,0,1,4,1,1,null,12,"",12,1,4,0,1,4,1,1]
[13,"",13,1,4,0,1,4,1,1,null,13,"",13,1,4,0,1,4,1,1]
[14,"",14,1,4,0,1,4,1,1,null,14,"",14,1,4,0,1,4,1,1]
[15,"",15,1,4,0,1,4,1,1,null,15,"",15,1,4,0,1,4,1,1]
[16,"",16,1,4,0,1,4,1,1,null,16,"",16,1,4,0,1,4,1,1]
[17,"",17,1,4,0,1,4,0,0,null,17,"",17,1,4,0,1,4,1,1]
[18,"",18,1,4,0,1,4,0,0,null,18,"",18,1,4,0,1,4,1,1]
[{"$nulls":11},19,"",19,1,4,0,1,4,1,1]
[{"$nulls":11},20,"",20,1,4,0,1,4,1,1]
[{"$nulls":11},21,"",21,1,4,0,1,4,1,1]
[{"$nulls":11},22,"",22,1,4,0,1,4,1,1]
[{"$nulls":11},23,"",23,1,4,0,1,4,1,1]
[{"$nulls":11},24,"",24,1,4,0,1,4,0,0]
[{"$nulls":11},25,"",25,1,4,0,1,4,1,0]
[]
[{"$nulls":15},11,null,2,1]
[{"$nulls":15},12,null,3,2]
[{"$nulls":15},13,null,4,3]
[{"$nulls":15},14,null,1,4]
[{"$nulls":15},21,null,4,2]
[{"$nulls":15},22,null,4,2]
[{"$nulls":15},23,null,1,1]
[{"$nulls":15},24,null,1,4]
[{"$nulls":15},31,null,3,3]
[{"$nulls":15},32,null,1,1]
[{"$nulls":15},33,null,3,3]
[{"$nulls":15},34,null,1,4]
[{"$nulls":15},41,null,1,4]
[{"$nulls":15},42,null,1,4]
[{"$nulls":15},43,null,1,4]
[{"$nulls":15},44,null,1,4]

{"sheet":"Matrix","index":30,"n_rows":6,"n_cols":6,"rows_kept":6,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[]
[]
[]
[]
[0,0,0,0,0,0]

{"sheet":"Comp Calc","index":31,"n_rows":72,"n_cols":30,"rows_kept":72,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,null,"SIMpull CU THHN","CU THHN","SIMpull CU XHHW","SIMpull AL THHN","AL XHHW","CU XHHW"]
[null,null,0,0,0,0,0,0,{"$nulls":4},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
["Allow Stress (lbs/cmil)","S",0.008,0.008,0.008,0.006,0.006,0.008,null,null,"Length","L",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
["Area of Conductor (cmil)","A",0,0,0,0,0,0,null,null,"Straight Section Radians","q",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
["Number of Conductors","N",0,0,0,0,0,0,null,null,"Bend Section Radians","f",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
["Wt Corr. Fct. ","w",1.4,1.4,1.4,1.4,1.4,1.4,null,null,"Bend Radius (ft)","R",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$error":"#VALUE!"}]
["Coefficient of Friction","m",0,0.35,0,0,0,0.35]
["Total Cable Wt. (Lbs/ft)","W",0,0,0,0,0,0,null,null,null,"SIMpull CU THHN",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
["Natural Logarithm base","e",2.718281828459045,2.718281828459045,2.718281828459045,2.718281828459045,2.718281828459045,2.718281828459045,null,null,null,"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Tension On Each Conductor (lbs)","TC",0,0,0,0,0,0,null,null,null,"Tension Out","","","","","","","","","","","","","","","","","",""]
["Max allowable tension on device (lbs)","Tcable",0,0,0,0,0,0,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Conduit Inner Diameter ","D",0.622,0.622,0.622,0.622,0.622,0.622,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Outter Diameter of Cable","d",0,0,0,0,0,0,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
["Conductor short circuit factor","Fc",0.0529,0.0529,0.0719,0.0346,0.047,0.0719,{"$nulls":4},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"t",0.1333,0.1333,0.1333,0.1333,0.1333,0.1333]
[null,"wm2",0,0.24009999999999992,0,0,0,0.24009999999999992,null,null,null,"Side Pressure","","","","","","","","","","","","","","","","","",""]
[]
[null,"Area of Conductor (cmil) for Short circuit calc",0,0,0,0,0,0]
[null,"Short Circuit Calc",0,0,0,0,0,0,null,null,null,"CU THHN",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[{"$nulls":11},"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Maximum Pulling Force (lb.)",0,0,0,0,0,0,null,null,null,"Tension Out","","","","","","","","","","","","","","","","","",""]
[null,"Max Sidewall Pres. (lb.)",0,500,0,0,0,500,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Total Ouside Diameter of Cable",0,0,0,0,0,0,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 1 in2",0,0,0,0,0,0,{"$nulls":4},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 2 in2",0,0,0,0,0,0]
[null,"Cable 3 in2",0,0,0,0,0,0,null,null,null,"Side Pressure","","","","","","","","","","","","","","","","","",""]
[null,"Cable Total in2",0,0,0,0,0,0]
[null,"Minimum Recommended Conduit Size",0.5,0.5,0.5,0.5,0.5,0.5]
[null,"Conduit Inner Diameter",0.622,0.622,0.622,0.622,0.622,0.622,null,null,null,"SIMpull AL THHN",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[{"$nulls":11},"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Ground Wire",0,0,0,0,0,0,null,null,null,"Tension Out","","","","","","","","","","","","","","","","","",""]
[null,"Fill Rate",0,0,0,0,0,0,{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,null,"0.5\" EMT (0% fill)","0.5\" EMT (0% fill)","0.5\" EMT (0% fill)","0.5\" EMT (0% fill)","0.5\" EMT (0% fill)","0.5\" EMT (0% fill)",{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 1 wt.",0,0,0,0,0,0,{"$nulls":4},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Cable 2 wt.",0,0,0,0,0,0]
[null,"Cable 3 wt.",0,0,0,0,0,0,null,null,null,"Side Pressure","","","","","","","","","","","","","","","","","",""]
[null,"Total wt.",0,0,0,0,0,0]
[]
[null,null,"SIMpull CU THHN","CU XHHW","CU USE","AL SIMpull THHN ","AL XHHW","AL USE",null,null,null," AL XHHW",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[null,"Maxis Grips Index","","","","","","",null,null,null,"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[null,"Maxis Grip Size","","","","","","",null,null,null,"Tension Out","","","","","","","","","","","","","","","","","",""]
[null,"Min Conduit Size","","","","","","",{"$nulls":4},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","",""]
[]
[]
[{"$nulls":11},"SIMpull CU XHHW",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[{"$nulls":11},"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":11},"Tension Out","","","","","","","","","","","","","","","","","",""]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","",""]
[]
[]
[{"$nulls":11},"CU XHHW",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
[{"$nulls":11},"Tension In",{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":11},"Tension Out","","","","","","","","","","","","","","","","","",""]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},25,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[{"$nulls":12},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
[{"$nulls":11},"Side Pressure","","","","","","","","","","","","","","","","","",""]

{"sheet":"PC REEL Size Data","index":32,"n_rows":43,"n_cols":40,"rows_kept":43,"cut":false,"hidden":true,"merged":[[1,11,7,11]],"flags":["formulas_cached_only"]}
["Reel Volume with 2\" clearance","Pkg-Id                             (diameter X width)","Max Wt. Capacity","Pkg / Tare Wt","Flange Dia","Drum Dia"]
[362715.7214128632,"R31 (108\" X 70.5\")",15000,1555,108,60,0,{"$nulls":32},1]
[362715.7214128632,"R38 (108\" X 73\")",20000,2387,108,60,2,{"$nulls":32},2]
[294524.3112740431,"R34 (104\" X 56.5\")",15000,1342,104,50,3,{"$nulls":32},3]
[270930.95044558373,"R29 (96\" X 62.5\")",15000,1195,96,48,4,{"$nulls":32},4]
[270930.95044558373,"R40 (96\" X 65\")",20000,1799,96,48,5,{"$nulls":32},5]
[234337.67921656984,"R30 (96\" X 62.5\")",12500,1237,96,60,6,{"$nulls":32},6]
[232226.5289533575,"R28 (96\" X 54.5\")",12500,1159,96,48,7,"Fits Blue A Frame",{"$nulls":31},7]
[205083.1684263417,"R27 (92\" X 54.5\")",12500,1082,92,48,8,"Fits Blue A Frame",{"$nulls":31},8]
[180151.4891274531,"R26 (84\" X 62\")",10000,877,84,48,9,{"$nulls":32},9]
[157582.28750406404,"R32 (78\" X 54\")",10000,763,78,36,10,{"$nulls":32},10]
[154415.5621092455,"R25 (84\" X 54\")",10000,847,84,48,11,"Fits Blue A Frame",{"$nulls":31},11]
[143558.21789843918,"R47 (84\" X 61.5)",6000,952,84,56,12,"Fits Blue A Frame",{"$nulls":31},12]
[118186.71562804801,"R22 (78\" X 42\")",8000,676,78,36,13,"Fits Blue A Frame",{"$nulls":31},13]
[115811.67158193413,"R24 (84\" X 42\")",10000,803,84,48,14,"Fits Blue A Frame",{"$nulls":31},14]
[94096.98316032148,"R20 (72\" X 42\")",8000,594,72,36,15,"Fits Blue A Frame",{"$nulls":31},15]
[89686.18707468141,"R23 (78\" 42\")",8000,710,78,48,16,"Fits Blue A Frame",{"$nulls":31},16]
[72043.00273212114,"N86 (66\" X 42\")",7500,536,66.1,36,17,"Fits Blue A Frame",{"$nulls":31},17]
[70874.33026498574,"R16 (66\" X 36\")",6000,385,66.1,32,18,"Fits 6' A Frame",{"$nulls":31},18]
[51723.18144870235,"A62A (60\" X 34\")",6800,397.45,60,28,19,"Fits 6' A Frame",{"$nulls":31},19]
[51529.97350050658,"N62 (58\" X 34.5\")",6500,303,58,27,20,"Fits 6' A Frame",{"$nulls":31},20]
[39466.25771072177,"N48 (50\" X 34\")",3500,198,50,21,21,"Fits 6' A Frame",{"$nulls":31},21]
[29907.96206217483,"N38 (48\" X 31.5\")",3500,165,48,24,22,"Fits 4' A Frame",{"$nulls":4},"A Frame information",{"$nulls":26},22]
[29907.96206217483,"C38A (48\" X 32\")",4800,195,48,24,23,"Fits 4' A Frame",{"$nulls":5},"4' X 4'","6' X 6\"","6' X 6\"-10\" (blue)",{"$nulls":23},23]
[27269.024233159405,"N35(45\" X 31\")",1500,122,45,21,24,"Fits 4' A Frame",{"$nulls":4},"Gross wt.","526#","530#","800#",{"$nulls":23},24]
[22870.794518133695,"N29C (42\" 29.5\")",3000,123.56,42,18,25,"Fits 4' A Frame",{"$nulls":4},"Max Diameter","48\"","66\"","96\"",{"$nulls":23},25]
[18981.50281298953,"N25F (40\" X 27.5\")",2500,111.16,40,18,26,"Fits 4' A Frame",{"$nulls":4},"Max Width","34\"","40\"","60\"",{"$nulls":23},26]
[14048.809647771857,"N19 (34\" X 29.5\")",1400,80,34,15,27,"Fits 4' A Frame",{"$nulls":4},"Max reel #","C38","R16","R28",{"$nulls":23},27]
[12139.11401347096,"C17 (34\" X 27.5\")",2500,99,34,16,28,"Fits 4' A Frame",{"$nulls":4}," Gross Wt Capacity","6000#","6000#","10,000#",{"$nulls":23},28]
[10159.91064170939,"N15 (32\" X 25\")",1250,55,32,14,29,"Fits 4' A Frame",{"$nulls":4},"Floor to Ctr of axle","30 .5\"","39\"","56.5\"",{"$nulls":23},29]
[5167.134516991812,"N7 (30\" X 20\")",950,45,30,17,30,"Fits 4' A Frame",{"$nulls":4},"Axle Diameter","2 7/8\"","2 7/8\"","2 7/8\"",{"$nulls":23},30]
[4251.654782781661,"N7P (23.75\"  X 25\")",800,47,23.75,12,31,"Fits 4' A Frame",{"$nulls":4},"Pallet Jack ID","25\"","25\"","N/A",{"$nulls":23},31]
[{"$nulls":12},"Pallet Jack OD","40\"","40\"","N/A"]
[{"$nulls":12},"Special notes:",null,"max of 7 per 48' ","Must ship empty"]
[]
[]
[]
[{"$nulls":12},"Trailer information"]
[{"$nulls":13},"Std","Special","Special request "]
[{"$nulls":12},"Length","48'","53'"]
[{"$nulls":12},"Width","8' 6\"","8' 6\""]
[{"$nulls":12},"Load Capacity","40,000#","40,000#"]
[{"$nulls":12},"Height"]